## TR81･82
⇒
High volt. Capacitor
Low volt. Capacitor
2002/08/01 Ver1.4
| Trunk number | Application section | Electric system | [5 empty] | Distribution side apparatus |  |  | Load side apparatus | [8 empty] | Selection-1 (Branch trunk) |  |  |  | Selection-2 (Trunk) |  |  |  | Transmission | Reception |  | Distribution |  | Note
|  |  | Sec. voltage ES[V] | [5 empty] | Power transformer |  | SCS Capacity | Load equipment capacity | [7 empty] | SCL Capacity | Cable name |  |  | Construct | Cable name |  |  | Construct | Voltage ER [V] | Voltage ＥＬ[V] | Current IL [A] | side |  |  | 1 phi-R | User-R | SCS | nphinW-1 | R-C1n | R-n2 | R-n4 |  |  | R-01 | E-Cn | Phi-G 20 | 負荷種別
|  |  | φ |  | W |  | V |  | Form | Number |  | Load classification | Output | Effici- ency | Power factor | Input | Demand factor | Load current | Ｚ Ｌ [Ω] |  | Cross | No. | Cable | Permission current[A] | Cross | No. | Cable | Permission current[A] | All load [A] | ＥＬ／Ｅ[％] | Current IC [A] | Breaker |  |  | 1 phi-X | User-X | SCLoad | nphinW-2 | X-C1n | X-n2 | X-n4 |  |  | X-01 |  | w-I20
Drop down LIST |  |  | Frequency [Hz] | [6 empty] | ％ Z | [Kvar] | [7 empty] | Ｒ Ｌ [Ω] | [Kvar] | section |  | span |  | section |  | span |  | TR current [A] | (Ｅ-ＥＬ)／Ｅ[％] | (Total) | Name |  |  | 3 phi-R | R-TR | R-n1 | R-n1' | R-C2n | R-n3 | R-n4' | R-n4' |  | R-02 | ES | E-K20
Load Classification |  |  | Calculation temp. | [5 empty] | Capacity/Rated current |  |  |  | [KW] | η | cosφ | [KVA] | Df | [A] | Ｘ Ｌ [Ω] | Avrg. PF | Ｚ Ｃ１ (Trunk) |  |  |  | Ｚ Ｃ２ (Branch trunk) |  |  |  | Branch part [V] | Zｎ１（Ｌｎ＋ＣＬ１） |  | -AF | -AT |  | 3 phi-X | X-TR | X-n1 | X-n1' | X-C2n | X-n3 | X-n4' | X-n4' |  | X-02 |  | Hz-G22
|  | No.8 Substation TR No.8-1 SC: 0KVar | [33 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
Prod. power | [35 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
Experimental eq. | [37 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
AC M/C | [37 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
Supply fan | 81L1 | No.8 Substation TR No8-1 Switchboard(Existing) ～#3S-1 | 1 | φ | 3 | W | 210 | V | (F)molded type | 1 |  | Lighting | 17.28 | 1 | 0.9 | 19.2 | 0.9 | 82.2857 | 0.92028 | [5 empty] | 600V CE(NE)-T |  |  |  | 102.0722 | 101.2534 | 220.0483 | MCCB-3P |  | Load factor of transformer | 1.35 | 0 | 0 | 2 |  | 0.68453 | 0.23871 |  |  | 0.23871 | 102.0722 | 1 | 0
Exhaust fan | [9 empty] | 5.0633 |  | Wall socket | 45.96 | 1 | 0.6 | 76.6 | 0.4 | 145.9048 | [10 empty] | 595.0841 | 96.4318 | 595.0841 |  |  | 62.48 ％ | 4.88 | 0 | 0 | 2 |  | 0.62618 | 0.24638 |  |  | 0.24638 |  | 3 | 0
|  |  | 50 | [5 empty] | 200 | [9 empty] | 0.67869 | 0.73748 |  |  |  |  | 200 | 2 | 55 |  | 595.0841 | 3.5682 |  | 400 | 400 |  | 0 | 0.0029767 | 0.67869 | 0.67869 | 0.121 | 0.23871 | 0.23871 |  | 0 | 0.24169 | 204.1444 | 210 | 0
sanitation |  |  | 50 | [5 empty] | 952.381 | [9 empty] | 0.62153 | [5 empty] | 5.8345 |  | 4.6475 |  |  | 0.67869 | 0.62153 |  |  |  | 0 | 0.01076 | 0.62153 | 0.62153 | 0.0845 | 0.24638 | 0.24638 |  | 1 | 0.25714 |  | 50 | 0
Septic tank | 81L2 | No.8 Substation TR No8-1 Switchboard(Existing) ～#3S-1 | [9 empty] | Lighting | 4.23 | 1 | 0.9 | 4.7 | 0.9 | 20.1429 | 1.1511 | [5 empty] | 600V CE(NE)-T |  |  |  | 102.0722 | 101.4273 | 176.2213 | MCCB-3P |  |  | 0 | 0 | 0 | 2 |  | 0.75072 | 0.36412 |  |  | 0.36412 | 102.0722 | 1 | 0
[12 empty] | Wall socket | 51.12 | 1 | 0.6 | 85.2 | 0.4 | 162.2857 | [11 empty] | 96.5974 | 375.6696 |  |  |  | 0 | 0 | 0 | 2 |  | 0.88229 | 0.40338 |  |  | 0.40338 |  | 3 | 0
[19 empty] | 0.74489 | 0.64709 |  |  |  |  | 200 | 2 | 55 |  |  | 3.4026 |  | 400 | 400 |  | 0 |  | 0.74489 | 0.74489 | 0.121 | 0.36412 | 0.36412 |  | 0 |  | 204.1444 | 210 | 0
Existing load |  |  | 50 | [15 empty] | 0.87764 | [5 empty] | 5.8345 |  | 4.6475 |  |  | 0.74489 | 0.87764 |  |  |  | 0 |  | 0.87764 | 0.87764 | 0.0845 | 0.40338 | 0.40338 |  | 1 |  |  | 50 | 0
| 81L3 | No.8 Substation TR No8-1 Switchboard(Existing) ～#3S-1 | [9 empty] | Lighting | 9.45 | 1 | 0.9 | 10.5 | 0.9 | 45 | 1.0154 | [5 empty] | 600V CE(NE)-T |  |  |  | 102.0722 | 101.3349 | 199.5908 | MCCB-3P |  |  | 0 | 0 | 0 | 2 |  | 0.70476 | 0.70476 |  |  | 0.70476 | 102.0722 | 1 | 0
[12 empty] | Wall socket | 50.97 | 1 | 0.6 | 84.95 | 0.4 | 161.8095 | [11 empty] | 96.5095 |  |  |  |  | 0 | 0 | 0 | 2 |  | 0.74126 | 0.74126 |  |  | 0.74126 |  | 3 | 0
Lighting Load | [18 empty] | 0.69893 | 0.68831 |  |  |  |  | 200 | 2 | 55 |  |  | 3.4905 |  | 400 | 400 |  | 0 |  | 0.69893 | 0.69893 | 0.121 | 0.70476 | 0.70476 |  | 0 |  | 204.1444 | 210 | 0
Wall socket |  |  | 50 | [15 empty] | 0.73661 | [5 empty] | 5.8345 |  | 4.6475 |  |  | 0.69893 | 0.73661 |  |  |  | 0 |  | 0.73661 | 0.73661 | 0.0845 | 0.74126 | 0.74126 |  | 1 |  |  | 50 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 2 |  |  | 0 | 0
|  | No.8 Substation TR No.8-2 SC: 0KVar | [33 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 3 |  |  | 0 | 0
| 82P1 | No.8 Substation TR No8-1 Switchboard(Existing) ～#3S-1 | 3 | φ | 3 | W | 210 | V | (F)molded type | 1 |  | Test machine | 7.8 | 0.8 | 0.8 | 12.1875 | 0.4 | 13.4028 | 1.2369 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.8149 | 203.7512 | 164.7302 | MCCB-3P |  | Load factor of transformer | 0 | 0 | 0 | 1.7321 |  | 0.99456 | 0.16103 |  |  | 0.16103 | 204.8149 | 3 | 0
[10 empty] | 4.2276 |  |  | 113.76 | 1 | 0.8 | 142.2 | 0.4 | 156.3794 | [10 empty] | 1017.7208 | 97.0244 | 1017.7208 |  |  | 74.03 ％ | 0 | 0 | 0 | 1 |  | 0.74615 | 0.12071 |  |  | 0.12071 |  | 3 | 0
|  |  | 50 | [5 empty] | 500 | [9 empty] | 0.9895 | 0.8 |  |  |  |  | 200 | 2 | 55 |  | 1017.7208 | 2.9756 |  | 400 | 400 |  | 1.07 | 0.0016346 | 0.9895 | 0.9895 | 0.121 | 0.16103 | 0.16103 |  | 0 | 0.16266 | 204.8149 | 210 | 0
|  |  | 50 | [5 empty] | 1374.6435 | [9 empty] | 0.74213 | [5 empty] | 5.0529 |  | 4.0249 |  |  | 0.9895 | 0.74213 |  |  |  | 4.09 | 0.0062482 | 0.74213 | 0.74213 | 0.0845 | 0.12071 | 0.12071 |  | 3 | 0.12696 |  | 50 | 0
Drop down LIST | 82P2 | No.8 Substation TR No8-1 Switchboard(Existing) ～#3S-1 | [9 empty] | Test machine | 4.9 | 0.8 | 0.8 | 7.6562 | 0.4 | 8.4197 | 1.2268 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.8149 | 203.7425 | 166.0768 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 0.98649 | 0.19214 |  |  | 0.19214 | 204.8149 | 3 | 0
construction of cable | [12 empty] | 118.4 | 1 | 0.8 | 148 | 0.4 | 162.7578 | [11 empty] | 97.0203 | 852.9907 |  |  |  | 0 | 0 | 0 | 1 |  | 0.7401 | 0.14401 |  |  | 0.14401 |  | 3 | 0
[19 empty] | 0.98144 | 0.8 |  |  |  |  | 200 | 2 | 55 |  |  | 2.9797 |  | 400 | 400 |  | 0 |  | 0.98144 | 0.98144 | 0.121 | 0.19214 | 0.19214 |  | 0 |  | 204.8149 | 210 | 0
Cabletray |  |  | 50 | [15 empty] | 0.73608 | [5 empty] | 5.0529 |  | 4.0249 |  |  | 0.98144 | 0.73608 |  |  |  | 0 |  | 0.73608 | 0.73608 | 0.0845 | 0.14401 | 0.14401 |  | 3 |  |  | 50 | 0
Subter- ranean | 82P3 | No.8 Substation TR No8-1 Switchboard(Existing) ～#3S-1 | [9 empty] | Test machine | 24 | 0.8 | 0.8 | 37.5 | 0.4 | 41.2393 | 1.5821 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.8149 | 203.3654 | 128.542 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.2739 | 0.23861 |  |  | 0.23861 | 204.8149 | 3 | 0
Under drain | [12 empty] | 66.56 | 1 | 0.8 | 83.2 | 0.4 | 91.4963 | [11 empty] | 96.8407 | 686.9139 |  |  |  | 0 | 0 | 0 | 1 |  | 0.95712 | 0.1788 |  |  | 0.1788 |  | 3 | 0
Openpit | [18 empty] | 1.2657 | 0.8 |  |  |  |  | 250 | 1 | 55 |  |  | 3.1593 |  | 400 | 400 |  | 0 |  | 1.2657 | 1.2657 | 0.0981 | 0.23861 | 0.23861 |  | 0 |  | 204.8149 | 210 | 0
Exposure piping |  |  | 50 | [15 empty] | 0.94926 | [5 empty] | 8.1932 |  | 7.8687 |  |  | 1.2657 | 0.94926 |  |  |  | 0 |  | 0.94926 | 0.94926 | 0.0826 | 0.1788 | 0.1788 |  | 3 |  |  | 50 | 0
Conceal. piping | 82P4 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.102 Oil pressure unit(G2-5) | [9 empty] | Test machine | 104 | 1 | 0.8 | 130 | 0.4 | 142.9629 | 1.4689 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.8149 | 203.3683 | 138.4482 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.1833 | 0.2936 |  |  | 0.2936 | 204.8149 | 3 | 0
[12 empty] | G2-5 | [17 empty] | 96.842 | 558.372 |  |  |  | 0 | 0 | 0 | 1 |  | 0.88786 | 0.21988 |  |  | 0.21988 |  | 3 | 0
[19 empty] | 1.1751 | 0.8 |  |  |  |  | 200 | 2 | 89 |  |  | 3.158 |  | 400 | 400 |  | 0 |  | 1.1751 | 1.1751 | 0.121 | 0.2936 | 0.2936 |  | 0 |  | 204.8149 | 210 | 0
|  |  | 50 | [15 empty] | 0.88135 | [5 empty] | 8.1764 |  | 6.5129 |  |  | 1.1751 | 0.88135 |  |  |  | 0 |  | 0.88135 | 0.88135 | 0.0845 | 0.21988 | 0.21988 |  | 3 |  |  | 50 | 0
| 82P5 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.102 VCF Tester(G2-8) | [9 empty] | Test machine | 56 | 1 | 0.8 | 70 | 0.4 | 76.98 | 2.728 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.8149 | 203.0412 | 74.4291 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 2.2029 | 0.39049 |  |  | 0.39049 | 204.8149 | 3 | 0
[12 empty] | G2-8 | [17 empty] | 96.6863 | 419.9238 |  |  |  | 0 | 0 | 0 | 1 |  | 1.6491 | 0.29225 |  |  | 0.29225 |  | 3 | 0
[19 empty] | 2.1824 | 0.8 |  |  |  |  | 150 | 1 | 85 |  |  | 3.3137 |  | 225 | 200 |  | 0 |  | 2.1824 | 2.1824 | 0.159 | 0.39049 | 0.39049 |  | 0 |  | 204.8149 | 210 | 0
|  |  | 50 | [15 empty] | 1.6368 | [5 empty] | 20.5227 |  | 12.3521 |  |  | 2.1824 | 1.6368 |  |  |  | 0 |  | 1.6368 | 1.6368 | 0.0839 | 0.29225 | 0.29225 |  | 3 |  |  | 50 | 0
| 82P6 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.106 CAE#2Tester(ATF-36) | [9 empty] | Test machine | 62.4 | 1 | 0.8 | 78 | 0.4 | 85.7778 | 2.4482 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.8149 | 202.7025 | 82.797 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.9805 | 0.47462 |  |  | 0.47462 | 204.8149 | 3 | 0
[12 empty] | ATF-36 | [17 empty] | 96.525 | 345.4947 |  |  |  | 0 | 0 | 0 | 1 |  | 1.4821 | 0.3552 |  |  | 0.3552 |  | 3 | 0
[19 empty] | 1.9585 | 0.8 |  |  |  |  | 150 | 1 | 91 |  |  | 3.475 |  | 225 | 225 |  | 0 |  | 1.9585 | 1.9585 | 0.159 | 0.47462 | 0.47462 |  | 0 |  | 204.8149 | 210 | 0
|  |  | 50 | [15 empty] | 1.4689 | [5 empty] | 21.9714 |  | 13.224 |  |  | 1.9585 | 1.4689 |  |  |  | 0 |  | 1.4689 | 1.4689 | 0.0839 | 0.3552 | 0.3552 |  | 3 |  |  | 50 | 0
| 82P7 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.106 CAE#2Tester(ATF-44) | [9 empty] | Test machine | 62.4 | 1 | 0.8 | 78 | 0.4 | 85.7778 | 2.4482 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.8149 | 202.7485 | 82.8158 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.98 | 0.62421 |  |  | 0.62421 | 204.8149 | 3 | 0
[12 empty] | ATF-44 | [17 empty] | 96.5469 | 262.6977 |  |  |  | 0 | 0 | 0 | 1 |  | 1.4818 | 0.46715 |  |  | 0.46715 |  | 3 | 0
[19 empty] | 1.9585 | 0.8 |  |  |  |  | 150 | 1 | 89 |  |  | 3.4531 |  | 225 | 225 |  | 0 |  | 1.9585 | 1.9585 | 0.159 | 0.62421 | 0.62421 |  | 0 |  | 204.8149 | 210 | 0
|  |  | 50 | [15 empty] | 1.4689 | [5 empty] | 21.4885 |  | 12.9334 |  |  | 1.9585 | 1.4689 |  |  |  | 0 |  | 1.4689 | 1.4689 | 0.0839 | 0.46715 | 0.46715 |  | 3 |  |  | 50 | 0
| 82P8 | No.8 Substation TR No8-1 Switchboard(Existing) ～#5P-1 | [9 empty] | Test machine | 4.7 | 0.8 | 0.8 | 7.3438 | 0.4 | 8.076 | 2.0883 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.8149 | 202.7193 | 97.0755 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.6892 | 0.9116 |  |  | 0.9116 | 204.8149 | 3 | 0
[13 empty] | 67.28 | 1 | 0.8 | 84.1 | 0.4 | 92.486 | [11 empty] | 96.533 | 179.8819 |  |  |  | 0 | 0 | 0 | 1 |  | 1.2641 | 0.68221 |  |  | 0.68221 |  | 3 | 0
[19 empty] | 1.6706 | 0.8 |  |  |  |  | 150 | 1 | 77 |  |  | 3.467 |  | 225 | 225 |  | 0 |  | 1.6706 | 1.6706 | 0.159 | 0.9116 | 0.9116 |  | 0 |  | 204.8149 | 210 | 0
|  |  | 50 | [15 empty] | 1.253 | [5 empty] | 18.5912 |  | 11.1896 |  |  | 1.6706 | 1.253 |  |  |  | 0 |  | 1.253 | 1.253 | 0.0839 | 0.68221 | 0.68221 |  | 3 |  |  | 50 | 0
| 82P9 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.106 Control board(G3-13) | [9 empty] | Test machine | 62.4 | 1 | 0.8 | 78 | 0.4 | 85.7778 | 2.4482 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.8149 | 202.7255 | 82.8064 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.9803 | 1.9803 |  |  | 1.9803 | 204.8149 | 3 | 0
[12 empty] | G3-13 | [17 empty] | 96.536 |  |  |  |  | 0 | 0 | 0 | 1 |  | 1.482 | 1.482 |  |  | 1.482 |  | 3 | 0
[19 empty] | 1.9585 | 0.8 |  |  |  |  | 150 | 1 | 90 |  |  | 3.464 |  | 225 | 225 |  | 0 |  | 1.9585 | 1.9585 | 0.159 | 1.9803 | 1.9803 |  | 0 |  | 204.8149 | 210 | 0
|  |  | 50 | [15 empty] | 1.4689 | [5 empty] | 21.73 |  | 13.0787 |  |  | 1.9585 | 1.4689 |  |  |  | 0 |  | 1.4689 | 1.4689 | 0.0839 | 1.482 | 1.482 |  | 3 |  |  | 50 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 4 |  |  | 0 | 0
[38 empty] | 1e+30 | [7 empty] | 0 | 0
|  | TGCRDL Relocation Project | [13 empty] | ESE-VD4 Exchange circuit analysis calculation | [5 empty] | Co.,Ltd. Yoshimura Airchitecture Design Office | [6 empty] | K,Yoshimura |  | K,Sakai |  |  | Terminal voltage -05 (Standard)
Note on B12: Drop down LIST An addition, change, and deletion can do this registration cell.
Note on B46: Drop down LIST An addition, change, and deletion can do this registration cell.
Note on C8: Printing range
Note on F13: Please input the temperature of conductor for calculation. (Each line) -100[℃] ～ +300[℃] Attention: It calculates by 0[℃] if it does not input. Ａｂｏｕｔ ｔｈｅ ｔｅｍｐｅｒａｔｕｒｅ ｏｆ ｃｏｎｄｕｃｔｏｒ The degree 20[℃] is standard temperature. Generally, this temperature is 50-60 [℃] except for a cold district. Please decide on reference by carrying out the maximum per- mission temperature of a conductor.
Note on L3: It can use for the power transmission voltage at the time of regular of an independent trunk and a branch trunk, received voltage, load current, the check of power factor, the determination of series capacitor capacity, etc. Comment ■ is the object for cells which needs an input． ■ is an explanatory note etc. Input cell ■ should input a required matter. Calculation cell ■ is an automatic calculation cell, an input is impossible.
Note on L11: ↓Please choose out of a drop down list. When Liszt does not have [except oil cooled type and (F)-molded type], please perform after inputting data into the "transformer USER" of DATA Table.
Note on L13: Following transformer data is registered into DATA Table. （50/60Hz） ３φ３Ｗ－２０ ～ １０００［ＫＶＡ］ １φ３Ｗ－１０ ～ ５００［ＫＶＡ］ An exact value will be calculated if the change correction of the %R and %X of an adoption transformer is made by DATA Table. Calculation of transformer rated current is depended below. In the case of ３φ：TRcap／(√3 x Es) In the case of １φ：TRcap／ Es TRcap：Capacity of TR. Es：Secondary voltage of TR.
Note on M11: When a transformer is parallel operation, please input the number of a parallel transformer.
Note on N6: High-voltage Capacitor［Nichicon Corp.1991.5］ 3300V，6600V-50Hz，60Hz（no Series reactor） 50, 75,100,150,200,250,300 [KVar] 3300V，6600V-50Hz，60Hz（Series reactor 6％） 50, 75,100,150,200,250,300,400,500,600, 700,750,800,900,1000[KVar] 3300V，6600V-50Hz，60Hz（Series reactor 13％） 50, 75,100,150,200,250,300,400,500[KVar]
Note on N7: Low-voltage Capacitor［Nichicon Corp.1991.5］ 200V，220V-50Hz，60Hz（no Series reactor） 10, 15, 20, 25, 30, 50[KVar] 200V，220V-50Hz，60Hz（Series reactor ６％） 10, 15, 20, 25, 30, 40, 50, 75,100[KVar] 400，415，440，460V-50Hz，60Hz（no Series reactor） 10, 15, 20, 25, 30, 50, 75,100,150[KVar] 400，415，440，460V-50Hz，60Hz（Series reactor 6％） 10, 15, 20, 25, 30, 50, 75,100,150,200 250,300[KVar]
Note on N10: Ｓｅｒｉｅｓ ｐｏｗｅｒ ｃａｐａｃｉｔｏｒ When average power factor of total load is bad (delay), SC improves power factor, and it installs the electric power transfor- mer by the side of power distribution in order to operate efficiently.
Note on O10: When you perform accumulation calculation, be careful of the following point. Trunk branch etc., when you accumulate the voltage drop value of each section, please use four lines each of a "cell" continuously. When you move to independent trunk calculation or next another calculation, four or more lines should vacate and please be sure to input a cell.
Note on O11: Please choose out of a drop down list.
Note on Q11: In the case of induction motor load, please input in the range of ０＜～１．０００ In the case of other loads, please input ”１”
Note on R11: Please input the value of the range of ０＜～１．０００
Note on S11: Iｎｐｕｔ ＫＶＡ Input ＫＶＡ＝Output ＫＷ／（ｃｏｓφｘη） cosφ ：Power factor of Load η ：Efficiency of Load
Note on W10: Load side Series Power Capacitor SC improves delay power factor of induc- tive load, reduces voltage drop of a trunk, and it installs it in order to prevent the fall of primary voltage.
Note on X11: Please choose out of a drop down list. In inputting the size which is not in a data table, please register R and X (50Hz) of the cable into a data table.
Note on Z11: Please input the fruit length meter of a cable.
Note on AA10: Please choose out of a drop down list.
Note on AB11: Please choose out of a drop down list. In inputting the size which is not in a data table, please register R and X (50Hz) of the cable into a data table.
Note on AD11: Please input the fruit length meter of a cable.
Note on AE10: Please choose out of a drop down list.
Note on AF10: Secondary transformer side voltage ［Ｖ］
Note on AF13: Voltage of the circuit diagram EB section ［Ｖ］
Note on AG11: Percent to power supply voltage [％]
Note on AG12: Percent of line voltage drop to power supply voltage [％]
Note on AJ11: ↓Please choose out of a drop down list. The important matter about selection of the frame / trip value of MCCB １） The check of interception capacity ２） The characteristic and the temperature conditions of MCCB ３） Grasp of the real load current which took into consideration the demand factor, load factor, divercity factor,voltage regulation rate of transformer, unbalance factor, etc. at the time of regular operation of a motor, at the time of starting of a motor. Frame value [A] of MCCB（Ｍｏｌｄｅｄ ｃａｓｅ ｃｉｒｃｕｉｔ ｂｒｅａｋｅｒ） ３０， ５０， ６０， １００， ２２５， ２５０， ４００， ６００， ８００，１０００， １２００，１６００，２０００，２５００，３０００， ３２００，４０００ Frame value [A] of ＡＣＢ（Ａｉｒ ｃｉｒｃｕｉｔ ｂｒｅａｋｅｒ） ６３０，１０００，１２５０，１６００，２０００， ２５００，３２００，４０００，５０００，６３００
Note on AJ12: Please choose out of a drop down list.
Note on AJ13: Please choose out of a drop down list.
Approved
Checked
Input cell
Exchange circuit analisys calculation -VD４
２００２ Ａｕｇ． Ｖｅｒ ２．0 by ＥＳＥ SERVICE
Automatic display
A "comment" will be displayed if cursor is brought close to the cell of upper right red.

## TR81･82SC
⇒
High volt. Capacitor
Low volt. Capacitor
2002/08/01 Ver1.4
| Trunk number | Application section | Electric system | [5 empty] | Distribution side apparatus |  |  | Load side apparatus | [8 empty] | Selection-1 (Branch trunk) |  |  |  | Selection-2 (Trunk) |  |  |  | Transmission | Reception |  | Distribution |  | Note
|  |  | Sec. voltage ES[V] | [5 empty] | Power transformer |  | SCS Capacity | Load equipment capacity | [7 empty] | SCL Capacity | Cable name |  |  | Construct | Cable name |  |  | Construct | Voltage ER [V] | Voltage ＥＬ[V] | Current IL [A] | side |  |  | 1 phi-R | User-R | SCS | nphinW-1 | R-C1n | R-n2 | R-n4 |  |  | R-01 | E-Cn | Phi-G 20 | 負荷種別
|  |  | φ |  | W |  | V |  | Form | Number |  | Load classification | Output | Effici- ency | Power factor | Input | Demand factor | Load current | Ｚ Ｌ [Ω] |  | Cross | No. | Cable | Permission current[A] | Cross | No. | Cable | Permission current[A] | All load [A] | ＥＬ／Ｅ[％] | Current IC [A] | Breaker |  |  | 1 phi-X | User-X | SCLoad | nphinW-2 | X-C1n | X-n2 | X-n4 |  |  | X-01 |  | w-I20
Drop down LIST |  |  | Frequency [Hz] | [6 empty] | ％ Z | [Kvar] | [7 empty] | Ｒ Ｌ [Ω] | [Kvar] | section |  | span |  | section |  | span |  | TR current [A] | (Ｅ-ＥＬ)／Ｅ[％] | (Total) | Name |  |  | 3 phi-R | R-TR | R-n1 | R-n1' | R-C2n | R-n3 | R-n4' | R-n4' |  | R-02 | ES | E-K20
Load Classification |  |  | Calculation temp. | [5 empty] | Capacity/Rated current |  |  |  | [KW] | η | cosφ | [KVA] | Df | [A] | Ｘ Ｌ [Ω] | Avrg. PF | Ｚ Ｃ１ (Trunk) |  |  |  | Ｚ Ｃ２ (Branch trunk) |  |  |  | Branch part [V] | Zｎ１（Ｌｎ＋ＣＬ１） |  | -AF | -AT |  | 3 phi-X | X-TR | X-n1 | X-n1' | X-C2n | X-n3 | X-n4' | X-n4' |  | X-02 |  | Hz-G22
|  | No.8 Substation TR No.8-1 SC: 50KVar | [33 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
Prod. power | [35 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
Experimental eq. | [37 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
AC M/C | [37 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
Supply fan | 81L1 | No.8 Substation TR No8-1 Switchboard(Existing) ～#3S-1 | 1 | φ | 3 | W | 210 | V | (F)molded type | 1 | 50 | Lighting | 17.28 | 1 | 0.9 | 19.2 | 0.9 | 82.2857 | 0.92028 | [5 empty] | 600V CE(NE)-T |  |  |  | 103.2913 | 102.4628 | 222.6765 | MCCB-3P |  | Load factor of transformer | 1.35 | 0 | 1.1338 | 2 |  | 0.68453 | 0.23871 |  |  | 0.40282 | 103.2913 | 1 | 0
Exhaust fan | [9 empty] | 5.0633 |  | Wall socket | 45.96 | 1 | 0.6 | 76.6 | 0.4 | 145.9048 | [10 empty] | 602.1915 | 97.5836 | 602.1915 |  |  | 48.67 ％ | 4.88 | 0 | 0 | 2 |  | 0.62618 | 0.24638 |  |  | 0.19059 |  | 3 | 0
|  |  | 50 | [5 empty] | 200 | [9 empty] | 0.67869 | 0.73748 |  |  |  |  | 200 | 2 | 55 |  | 463.5718 | 2.4164 |  | 400 | 400 |  | 0 | 0.0029767 | 0.67869 | 0.67869 | 0.121 | 0.23871 | 0.23871 |  | 0 | 0.40579 | 206.5826 | 210 | 0
sanitation |  |  | 50 | [5 empty] | 952.381 | [9 empty] | 0.62153 | [5 empty] | 5.8345 |  | 4.6475 |  |  | 0.67869 | 0.62153 |  |  |  | 0 | 0.01076 | 0.62153 | 0.62153 | 0.0845 | 0.24638 | 0.24638 |  | 1 | 0.20135 |  | 50 | 0
Septic tank | 81L2 | No.8 Substation TR No8-1 Switchboard(Existing) ～#3S-1 | [9 empty] | Lighting | 4.23 | 1 | 0.9 | 4.7 | 0.9 | 20.1429 | 1.1511 | [5 empty] | 600V CE(NE)-T |  |  |  | 103.2913 | 102.6387 | 178.326 | MCCB-3P |  |  | 0 | 0 | 0 | 2 |  | 0.75072 | 0.36412 |  |  | 0.36412 | 103.2913 | 1 | 0
[12 empty] | Wall socket | 51.12 | 1 | 0.6 | 85.2 | 0.4 | 162.2857 | [11 empty] | 97.7511 | 380.1565 |  |  |  | 0 | 0 | 0 | 2 |  | 0.88229 | 0.40338 |  |  | 0.40338 |  | 3 | 0
[19 empty] | 0.74489 | 0.64709 |  |  |  |  | 200 | 2 | 55 |  |  | 2.2489 |  | 400 | 400 |  | 0 |  | 0.74489 | 0.74489 | 0.121 | 0.36412 | 0.36412 |  | 0 |  | 206.5826 | 210 | 0
Existing load |  |  | 50 | [15 empty] | 0.87764 | [5 empty] | 5.8345 |  | 4.6475 |  |  | 0.74489 | 0.87764 |  |  |  | 0 |  | 0.87764 | 0.87764 | 0.0845 | 0.40338 | 0.40338 |  | 1 |  |  | 50 | 0
| 81L3 | No.8 Substation TR No8-1 Switchboard(Existing) ～#3S-1 | [9 empty] | Lighting | 9.45 | 1 | 0.9 | 10.5 | 0.9 | 45 | 1.0154 | [5 empty] | 600V CE(NE)-T |  |  |  | 103.2913 | 102.5452 | 201.9746 | MCCB-3P |  |  | 0 | 0 | 0 | 2 |  | 0.70476 | 0.70476 |  |  | 0.70476 | 103.2913 | 1 | 0
[12 empty] | Wall socket | 50.97 | 1 | 0.6 | 84.95 | 0.4 | 161.8095 | [11 empty] | 97.6621 |  |  |  |  | 0 | 0 | 0 | 2 |  | 0.74126 | 0.74126 |  |  | 0.74126 |  | 3 | 0
Lighting Load | [18 empty] | 0.69893 | 0.68831 |  |  |  |  | 200 | 2 | 55 |  |  | 2.3379 |  | 400 | 400 |  | 0 |  | 0.69893 | 0.69893 | 0.121 | 0.70476 | 0.70476 |  | 0 |  | 206.5826 | 210 | 0
Wall socket |  |  | 50 | [15 empty] | 0.73661 | [5 empty] | 5.8345 |  | 4.6475 |  |  | 0.69893 | 0.73661 |  |  |  | 0 |  | 0.73661 | 0.73661 | 0.0845 | 0.74126 | 0.74126 |  | 1 |  |  | 50 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 2 |  |  | 0 | 0
|  | No.8 Substation TR No.8-2 SC:150KVar | [33 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 3 |  |  | 0 | 0
| 82P1 | No.8 Substation TR No8-1 Switchboard(Existing) ～#3S-1 | 3 | φ | 3 | W | 210 | V | (F)molded type | 1 | 150 | Test machine | 7.8 | 0.8 | 0.8 | 12.1875 | 0.4 | 13.4028 | 1.2369 | [5 empty] | 600V CE(NE)-T |  |  |  | 207.2812 | 206.2047 | 166.7137 | MCCB-3P |  | Load factor of transformer | 0 | 0 | 1.9638 | 1.7321 |  | 0.99456 | 0.16103 |  |  | 0.23608 | 207.2812 | 3 | 0
[10 empty] | 4.2276 |  |  | 113.76 | 1 | 0.8 | 142.2 | 0.4 | 156.3794 | [10 empty] | 1029.9755 | 98.1927 | 1029.9755 |  |  | 61.88 ％ | 0 | 0 | 0 | 1 |  | 0.74615 | 0.12071 |  |  | 0.060369 |  | 3 | 0
|  |  | 50 | [5 empty] | 500 | [9 empty] | 0.9895 | 0.8 |  |  |  |  | 200 | 2 | 55 |  | 850.6417 | 1.8073 |  | 400 | 400 |  | 1.07 | 0.0016346 | 0.9895 | 0.9895 | 0.121 | 0.16103 | 0.16103 |  | 0 | 0.23771 | 207.2812 | 210 | 0
|  |  | 50 | [5 empty] | 1374.6435 | [9 empty] | 0.74213 | [5 empty] | 5.0529 |  | 4.0249 |  |  | 0.9895 | 0.74213 |  |  |  | 4.09 | 0.0062482 | 0.74213 | 0.74213 | 0.0845 | 0.12071 | 0.12071 |  | 3 | 0.066617 |  | 50 | 0
Drop down LIST | 82P2 | No.8 Substation TR No8-1 Switchboard(Existing) ～#3S-1 | [9 empty] | Test machine | 4.9 | 0.8 | 0.8 | 7.6562 | 0.4 | 8.4197 | 1.2268 | [5 empty] | 600V CE(NE)-T |  |  |  | 207.2812 | 206.1959 | 168.0766 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 0.98649 | 0.19214 |  |  | 0.19214 | 207.2812 | 3 | 0
construction of cable | [12 empty] | 118.4 | 1 | 0.8 | 148 | 0.4 | 162.7578 | [11 empty] | 98.1885 | 863.2618 |  |  |  | 0 | 0 | 0 | 1 |  | 0.7401 | 0.14401 |  |  | 0.14401 |  | 3 | 0
[19 empty] | 0.98144 | 0.8 |  |  |  |  | 200 | 2 | 55 |  |  | 1.8115 |  | 400 | 400 |  | 0 |  | 0.98144 | 0.98144 | 0.121 | 0.19214 | 0.19214 |  | 0 |  | 207.2812 | 210 | 0
Cabletray |  |  | 50 | [15 empty] | 0.73608 | [5 empty] | 5.0529 |  | 4.0249 |  |  | 0.98144 | 0.73608 |  |  |  | 0 |  | 0.73608 | 0.73608 | 0.0845 | 0.14401 | 0.14401 |  | 3 |  |  | 50 | 0
Subter- ranean | 82P3 | No.8 Substation TR No8-1 Switchboard(Existing) ～#3S-1 | [9 empty] | Test machine | 24 | 0.8 | 0.8 | 37.5 | 0.4 | 41.2393 | 1.5821 | [5 empty] | 600V CE(NE)-T |  |  |  | 207.2812 | 205.8142 | 130.0899 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.2739 | 0.23861 |  |  | 0.23861 | 207.2812 | 3 | 0
Under drain | [12 empty] | 66.56 | 1 | 0.8 | 83.2 | 0.4 | 91.4963 | [11 empty] | 98.0068 | 695.1852 |  |  |  | 0 | 0 | 0 | 1 |  | 0.95712 | 0.1788 |  |  | 0.1788 |  | 3 | 0
Openpit | [18 empty] | 1.2657 | 0.8 |  |  |  |  | 250 | 1 | 55 |  |  | 1.9932 |  | 400 | 400 |  | 0 |  | 1.2657 | 1.2657 | 0.0981 | 0.23861 | 0.23861 |  | 0 |  | 207.2812 | 210 | 0
Exposure piping |  |  | 50 | [15 empty] | 0.94926 | [5 empty] | 8.1932 |  | 7.8687 |  |  | 1.2657 | 0.94926 |  |  |  | 0 |  | 0.94926 | 0.94926 | 0.0826 | 0.1788 | 0.1788 |  | 3 |  |  | 50 | 0
Conceal. piping | 82P4 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.102 Oil pressure unit(G2-5) | [9 empty] | Test machine | 104 | 1 | 0.8 | 130 | 0.4 | 142.9629 | 1.4689 | [5 empty] | 600V CE(NE)-T |  |  |  | 207.2812 | 205.8171 | 140.1153 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.1833 | 0.2936 |  |  | 0.2936 | 207.2812 | 3 | 0
[12 empty] | G2-5 | [17 empty] | 98.0081 | 565.0955 |  |  |  | 0 | 0 | 0 | 1 |  | 0.88786 | 0.21988 |  |  | 0.21988 |  | 3 | 0
[19 empty] | 1.1751 | 0.8 |  |  |  |  | 200 | 2 | 89 |  |  | 1.9919 |  | 400 | 400 |  | 0 |  | 1.1751 | 1.1751 | 0.121 | 0.2936 | 0.2936 |  | 0 |  | 207.2812 | 210 | 0
|  |  | 50 | [15 empty] | 0.88135 | [5 empty] | 8.1764 |  | 6.5129 |  |  | 1.1751 | 0.88135 |  |  |  | 0 |  | 0.88135 | 0.88135 | 0.0845 | 0.21988 | 0.21988 |  | 3 |  |  | 50 | 0
| 82P5 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.102 VCF Tester(G2-8) | [9 empty] | Test machine | 56 | 1 | 0.8 | 70 | 0.4 | 76.98 | 2.728 | [5 empty] | 600V CE(NE)-T |  |  |  | 207.2812 | 205.4861 | 75.3254 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 2.2029 | 0.39049 |  |  | 0.39049 | 207.2812 | 3 | 0
[12 empty] | G2-8 | [17 empty] | 97.8505 | 424.9803 |  |  |  | 0 | 0 | 0 | 1 |  | 1.6491 | 0.29225 |  |  | 0.29225 |  | 3 | 0
[19 empty] | 2.1824 | 0.8 |  |  |  |  | 150 | 1 | 85 |  |  | 2.1495 |  | 225 | 200 |  | 0 |  | 2.1824 | 2.1824 | 0.159 | 0.39049 | 0.39049 |  | 0 |  | 207.2812 | 210 | 0
|  |  | 50 | [15 empty] | 1.6368 | [5 empty] | 20.5227 |  | 12.3521 |  |  | 2.1824 | 1.6368 |  |  |  | 0 |  | 1.6368 | 1.6368 | 0.0839 | 0.29225 | 0.29225 |  | 3 |  |  | 50 | 0
| 82P6 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.106 CAE#2Tester(ATF-36) | [9 empty] | Test machine | 62.4 | 1 | 0.8 | 78 | 0.4 | 85.7778 | 2.4482 | [5 empty] | 600V CE(NE)-T |  |  |  | 207.2812 | 205.1433 | 83.794 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.9805 | 0.47462 |  |  | 0.47462 | 207.2812 | 3 | 0
[12 empty] | ATF-36 | [17 empty] | 97.6873 | 349.6549 |  |  |  | 0 | 0 | 0 | 1 |  | 1.4821 | 0.3552 |  |  | 0.3552 |  | 3 | 0
[19 empty] | 1.9585 | 0.8 |  |  |  |  | 150 | 1 | 91 |  |  | 2.3127 |  | 225 | 225 |  | 0 |  | 1.9585 | 1.9585 | 0.159 | 0.47462 | 0.47462 |  | 0 |  | 207.2812 | 210 | 0
|  |  | 50 | [15 empty] | 1.4689 | [5 empty] | 21.9714 |  | 13.224 |  |  | 1.9585 | 1.4689 |  |  |  | 0 |  | 1.4689 | 1.4689 | 0.0839 | 0.3552 | 0.3552 |  | 3 |  |  | 50 | 0
| 82P7 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.106 CAE#2Tester(ATF-44) | [9 empty] | Test machine | 62.4 | 1 | 0.8 | 78 | 0.4 | 85.7778 | 2.4482 | [5 empty] | 600V CE(NE)-T |  |  |  | 207.2812 | 205.1899 | 83.813 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.98 | 0.62421 |  |  | 0.62421 | 207.2812 | 3 | 0
[12 empty] | ATF-44 | [17 empty] | 97.7095 | 265.8609 |  |  |  | 0 | 0 | 0 | 1 |  | 1.4818 | 0.46715 |  |  | 0.46715 |  | 3 | 0
[19 empty] | 1.9585 | 0.8 |  |  |  |  | 150 | 1 | 89 |  |  | 2.2905 |  | 225 | 225 |  | 0 |  | 1.9585 | 1.9585 | 0.159 | 0.62421 | 0.62421 |  | 0 |  | 207.2812 | 210 | 0
|  |  | 50 | [15 empty] | 1.4689 | [5 empty] | 21.4885 |  | 12.9334 |  |  | 1.9585 | 1.4689 |  |  |  | 0 |  | 1.4689 | 1.4689 | 0.0839 | 0.46715 | 0.46715 |  | 3 |  |  | 50 | 0
| 82P8 | No.8 Substation TR No8-1 Switchboard(Existing) ～#5P-1 | [9 empty] | Test machine | 4.7 | 0.8 | 0.8 | 7.3438 | 0.4 | 8.076 | 2.0883 | [5 empty] | 600V CE(NE)-T |  |  |  | 207.2812 | 205.1603 | 98.2445 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.6892 | 0.9116 |  |  | 0.9116 | 207.2812 | 3 | 0
[13 empty] | 67.28 | 1 | 0.8 | 84.1 | 0.4 | 92.486 | [11 empty] | 97.6954 | 182.0479 |  |  |  | 0 | 0 | 0 | 1 |  | 1.2641 | 0.68221 |  |  | 0.68221 |  | 3 | 0
[19 empty] | 1.6706 | 0.8 |  |  |  |  | 150 | 1 | 77 |  |  | 2.3046 |  | 225 | 225 |  | 0 |  | 1.6706 | 1.6706 | 0.159 | 0.9116 | 0.9116 |  | 0 |  | 207.2812 | 210 | 0
|  |  | 50 | [15 empty] | 1.253 | [5 empty] | 18.5912 |  | 11.1896 |  |  | 1.6706 | 1.253 |  |  |  | 0 |  | 1.253 | 1.253 | 0.0839 | 0.68221 | 0.68221 |  | 3 |  |  | 50 | 0
| 82P9 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.106 Control board(G3-13) | [9 empty] | Test machine | 62.4 | 1 | 0.8 | 78 | 0.4 | 85.7778 | 2.4482 | [5 empty] | 600V CE(NE)-T |  |  |  | 207.2812 | 205.1666 | 83.8035 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.9803 | 1.9803 |  |  | 1.9803 | 207.2812 | 3 | 0
[12 empty] | G3-13 | [17 empty] | 97.6984 |  |  |  |  | 0 | 0 | 0 | 1 |  | 1.482 | 1.482 |  |  | 1.482 |  | 3 | 0
[19 empty] | 1.9585 | 0.8 |  |  |  |  | 150 | 1 | 90 |  |  | 2.3016 |  | 225 | 225 |  | 0 |  | 1.9585 | 1.9585 | 0.159 | 1.9803 | 1.9803 |  | 0 |  | 207.2812 | 210 | 0
|  |  | 50 | [15 empty] | 1.4689 | [5 empty] | 21.73 |  | 13.0787 |  |  | 1.9585 | 1.4689 |  |  |  | 0 |  | 1.4689 | 1.4689 | 0.0839 | 1.482 | 1.482 |  | 3 |  |  | 50 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 4 |  |  | 0 | 0
[38 empty] | 1e+30 | [7 empty] | 0 | 0
|  | TGCRDL Relocation Project | [13 empty] | ESE-VD4 Exchange circuit analysis calculation | [5 empty] | Co.,Ltd. Yoshimura Airchitecture Design Office | [6 empty] | K,Yoshimura |  | K,Sakai |  |  | Terminal voltage -06 (Standard)
Note on B12: Drop down LIST An addition, change, and deletion can do this registration cell.
Note on B46: Drop down LIST An addition, change, and deletion can do this registration cell.
Note on C8: Printing range
Note on F13: Please input the temperature of conductor for calculation. (Each line) -100[℃] ～ +300[℃] Attention: It calculates by 0[℃] if it does not input. Ａｂｏｕｔ ｔｈｅ ｔｅｍｐｅｒａｔｕｒｅ ｏｆ ｃｏｎｄｕｃｔｏｒ The degree 20[℃] is standard temperature. Generally, this temperature is 50-60 [℃] except for a cold district. Please decide on reference by carrying out the maximum per- mission temperature of a conductor.
Note on L3: It can use for the power transmission voltage at the time of regular of an independent trunk and a branch trunk, received voltage, load current, the check of power factor, the determination of series capacitor capacity, etc. Comment ■ is the object for cells which needs an input． ■ is an explanatory note etc. Input cell ■ should input a required matter. Calculation cell ■ is an automatic calculation cell, an input is impossible.
Note on L11: ↓Please choose out of a drop down list. When Liszt does not have [except oil cooled type and (F)-molded type], please perform after inputting data into the "transformer USER" of DATA Table.
Note on L13: Following transformer data is registered into DATA Table. （50/60Hz） ３φ３Ｗ－２０ ～ １０００［ＫＶＡ］ １φ３Ｗ－１０ ～ ５００［ＫＶＡ］ An exact value will be calculated if the change correction of the %R and %X of an adoption transformer is made by DATA Table. Calculation of transformer rated current is depended below. In the case of ３φ：TRcap／(√3 x Es) In the case of １φ：TRcap／ Es TRcap：Capacity of TR. Es：Secondary voltage of TR.
Note on M11: When a transformer is parallel operation, please input the number of a parallel transformer.
Note on N6: High-voltage Capacitor［Nichicon Corp.1991.5］ 3300V，6600V-50Hz，60Hz（no Series reactor） 50, 75,100,150,200,250,300 [KVar] 3300V，6600V-50Hz，60Hz（Series reactor 6％） 50, 75,100,150,200,250,300,400,500,600, 700,750,800,900,1000[KVar] 3300V，6600V-50Hz，60Hz（Series reactor 13％） 50, 75,100,150,200,250,300,400,500[KVar]
Note on N7: Low-voltage Capacitor［Nichicon Corp.1991.5］ 200V，220V-50Hz，60Hz（no Series reactor） 10, 15, 20, 25, 30, 50[KVar] 200V，220V-50Hz，60Hz（Series reactor ６％） 10, 15, 20, 25, 30, 40, 50, 75,100[KVar] 400，415，440，460V-50Hz，60Hz（no Series reactor） 10, 15, 20, 25, 30, 50, 75,100,150[KVar] 400，415，440，460V-50Hz，60Hz（Series reactor 6％） 10, 15, 20, 25, 30, 50, 75,100,150,200 250,300[KVar]
Note on N10: Ｓｅｒｉｅｓ ｐｏｗｅｒ ｃａｐａｃｉｔｏｒ When average power factor of total load is bad (delay), SC improves power factor, and it installs the electric power transfor- mer by the side of power distribution in order to operate efficiently.
Note on O10: When you perform accumulation calculation, be careful of the following point. Trunk branch etc., when you accumulate the voltage drop value of each section, please use four lines each of a "cell" continuously. When you move to independent trunk calculation or next another calculation, four or more lines should vacate and please be sure to input a cell.
Note on O11: Please choose out of a drop down list.
Note on Q11: In the case of induction motor load, please input in the range of ０＜～１．０００ In the case of other loads, please input ”１”
Note on R11: Please input the value of the range of ０＜～１．０００
Note on S11: Iｎｐｕｔ ＫＶＡ Input ＫＶＡ＝Output ＫＷ／（ｃｏｓφｘη） cosφ ：Power factor of Load η ：Efficiency of Load
Note on W10: Load side Series Power Capacitor SC improves delay power factor of induc- tive load, reduces voltage drop of a trunk, and it installs it in order to prevent the fall of primary voltage.
Note on X11: Please choose out of a drop down list. In inputting the size which is not in a data table, please register R and X (50Hz) of the cable into a data table.
Note on Z11: Please input the fruit length meter of a cable.
Note on AA10: Please choose out of a drop down list.
Note on AB11: Please choose out of a drop down list. In inputting the size which is not in a data table, please register R and X (50Hz) of the cable into a data table.
Note on AD11: Please input the fruit length meter of a cable.
Note on AE10: Please choose out of a drop down list.
Note on AF10: Secondary transformer side voltage ［Ｖ］
Note on AF13: Voltage of the circuit diagram EB section ［Ｖ］
Note on AG11: Percent to power supply voltage [％]
Note on AG12: Percent of line voltage drop to power supply voltage [％]
Note on AJ11: ↓Please choose out of a drop down list. The important matter about selection of the frame / trip value of MCCB １） The check of interception capacity ２） The characteristic and the temperature conditions of MCCB ３） Grasp of the real load current which took into consideration the demand factor, load factor, divercity factor,voltage regulation rate of transformer, unbalance factor, etc. at the time of regular operation of a motor, at the time of starting of a motor. Frame value [A] of MCCB（Ｍｏｌｄｅｄ ｃａｓｅ ｃｉｒｃｕｉｔ ｂｒｅａｋｅｒ） ３０， ５０， ６０， １００， ２２５， ２５０， ４００， ６００， ８００，１０００， １２００，１６００，２０００，２５００，３０００， ３２００，４０００ Frame value [A] of ＡＣＢ（Ａｉｒ ｃｉｒｃｕｉｔ ｂｒｅａｋｅｒ） ６３０，１０００，１２５０，１６００，２０００， ２５００，３２００，４０００，５０００，６３００
Note on AJ12: Please choose out of a drop down list.
Note on AJ13: Please choose out of a drop down list.
Approved
Checked
Input cell
Exchange circuit analisys calculation -VD４
２００２ Ａｕｇ． Ｖｅｒ ２．0 by ＥＳＥ SERVICE
Automatic display
A "comment" will be displayed if cursor is brought close to the cell of upper right red.

## 3S-1(L)
⇒
3.4278
High volt. Capacitor
Low volt. Capacitor
2002/08/01 Ver1.4
| Trunk number | Application section | Electric system | [5 empty] | Distribution side apparatus |  |  | Load side apparatus | [8 empty] | Selection-1 (Branch trunk) |  |  |  | Selection-2 (Trunk) |  |  |  | Transmission | Reception |  | Distribution |  | Note
|  |  | Sec. voltage ES[V] | [5 empty] | Power transformer |  | SCS Capacity | Load equipment capacity | [7 empty] | SCL Capacity | Cable name |  |  | Construct | Cable name |  |  | Construct | Voltage ER [V] | Voltage ＥＬ[V] | Current IL [A] | side |  |  | 1 phi-R | User-R | SCS | nphinW-1 | R-C1n | R-n2 | R-n4 |  |  | R-01 | E-Cn | Phi-G 20 | Load classification
|  |  | φ |  | W |  | V |  | Form | Number |  | Load classification | Output | Effici- ency | Power factor | Input | Demand factor | Load current | Ｚ Ｌ [Ω] |  | Cross | No. | Cable | Permission current[A] | Cross | No. | Cable | Permission current[A] | All load [A] | ＥＬ／Ｅ[％] | Current IC [A] | Breaker |  |  | 1 phi-X | User-X | SCLoad | nphinW-2 | X-C1n | X-n2 | X-n4 |  |  | X-01 |  | w-I20
Drop down LIST |  |  | Frequency [Hz] | [6 empty] | ％ Z | [Kvar] | [7 empty] | Ｒ Ｌ [Ω] | [Kvar] | section |  | span |  | section |  | span |  | TR current [A] | (Ｅ-ＥＬ)／Ｅ[％] | (Total) | Name |  |  | 3 phi-R | R-TR | R-n1 | R-n1' | R-C2n | R-n3 | R-n4' | R-n4' |  | R-02 | ES | E-K20
Load Classification |  |  | Calculation temp. | [5 empty] | Capacity/Rated current |  |  |  | [KW] | η | cosφ | [KVA] | Df | [A] | Ｘ Ｌ [Ω] | Avrg. PF | Ｚ Ｃ１ (Trunk) |  |  |  | Ｚ Ｃ２ (Branch trunk) |  |  |  | Branch part [V] | Zｎ１（Ｌｎ＋ＣＬ１） |  | -AF | -AT |  | 3 phi-X | X-TR | X-n1 | X-n1' | X-C2n | X-n3 | X-n4' | X-n4' |  | X-02 |  | Hz-G22
|  | No.8 Substation TR No.8-1 #3S-1 Secondary side | [33 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
Prod. power | [35 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
Experimental eq. | [37 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
AC M/C | [37 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
Supply fan | 81L1 -01 | No.8 Substation TR No8-1 #3S-1 ～#3L-12 | 1 | φ | 3 | W | 202.7 | V | (F)molded type | 1 |  | Lighting | 4.815 | 1 | 0.9 | 5.35 | 0.9 | 23.7543 | 6.5898 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray | 98.5188 | 97.9123 | 29.7164 | MCCB-3P |  |  | 1.35 | 0 | 0 | 2 | 0.626 | 5.619 | 0.22254 | 0.23657 |  | 0.22254 | 98.0839 | 1 | 0
Exhaust fan | [9 empty] | 5.0633 |  | Wall socket | 2.13 | 1 | 0.6 | 3.55 | 0.4 | 7.0054 | [10 empty] | 619.2534 | 96.6081 | 619.2534 |  |  |  | 4.88 | 0 | 0 | 2 | 0.0939 | 3.4647 | 0.22742 | 0.24942 |  | 0.22742 |  | 3 | 0
|  |  | 50 | [5 empty] | 200 | [9 empty] | 5.606 | 0.85071 | 38 | 1 | 17 |  | 14 | 1 | 4 |  | 619.2534 | 3.3919 |  | 100 | 75 |  | 0 | 0.0027734 | 5.606 | 5.606 | 1.71 | 3.4278 | 3.4481 | 0.22254 | 0 | 0.22531 | 197.0377 | 202.7 | 0
sanitation |  |  | 75 | [5 empty] | 986.6798 | [9 empty] | 3.4638 |  | 20.3 |  | 3.1926 |  | 13.0476 |  | 0.856 |  |  | 5.606 | 3.4638 |  |  |  | 0 | 0.010025 | 3.4638 | 3.4638 | 0.107 | 2.3803 | 2.3835 | 0.22742 | 1 | 0.23744 |  | 50 | 0
Septic tank |  | #3L-12 ～#3L-11 | [9 empty] | Lighting | 1.62 | 1 | 0.9 | 1.8 | 0.9 | 7.9921 | 11.226 | [5 empty] | 600V CV-T |  |  | Cable -tray |  | 97.7176 | 17.4091 |  |  |  | 0 | 0 | 0 | 2 |  | 8.6186 | 8.6186 |  |  | 8.6186 | 98.0839 | 1 | 0
[12 empty] | Wall socket | 3.06 | 1 | 0.6 | 5.1 | 0.4 | 10.0641 | [11 empty] | 96.416 | 17.4091 |  |  |  | 0 | 0 | 0 | 2 |  | 7.2588 | 7.2588 |  |  | 7.2588 |  | 3 | 0
[19 empty] | 8.5664 | 0.76309 |  |  |  |  | 14 | 1 | 16 |  |  | 3.584 |  |  |  |  | 0 |  | 8.5664 | 8.5664 | 1.71 | 8.6186 | 8.6186 |  | 0 |  | 197.0377 | 202.7 | 0
Existing load |  |  | 75 | [15 empty] | 7.2553 | [5 empty] | 52.1902 |  | 3.424 |  | 98.0839 | 8.5664 | 7.2553 |  |  |  | 0 |  | 7.2553 | 7.2553 | 0.107 | 7.2588 | 7.2588 |  | 1 |  |  | 50 | 0
| 81L1 -02 | No.8 Substation TR No8-1 #3S-1 ～#3L-13 | [9 empty] | Lighting | 2.07 | 1 | 0.9 | 2.3 | 0.9 | 10.2121 | 8.5777 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray | 98.5188 | 97.7526 | 22.7922 | MCCB-3P |  |  | 0 | 0 | 0 | 2 | 0.626 | 6.5314 | 0.23657 | 0.25575 |  | 0.23657 | 97.8719 | 1 | 0
[12 empty] | Wall socket | 4.08 | 1 | 0.6 | 6.8 | 0.4 | 13.4188 | [11 empty] | 96.4505 | 569.4118 |  |  |  | 0 | 0 | 0 | 2 | 0.0939 | 5.5766 | 0.24942 | 0.27473 |  | 0.24942 |  | 3 | 0
Lighting Load | [18 empty] | 6.5183 | 0.75991 | 38 | 1 | 26 |  | 14 | 1 | 4 |  |  | 3.5495 |  | 100 | 75 |  | 0 |  | 6.5183 | 6.5183 | 1.71 | 3.0485 | 3.0795 | 0.23657 | 0 |  | 197.0377 | 202.7 | 0
Wall socket |  |  | 75 | [15 empty] | 5.5757 |  | 31.0471 |  | 4.8828 |  | 13.0476 |  | 0.856 |  |  | 6.5183 | 5.5757 |  |  |  | 0 |  | 5.5757 | 5.5757 | 0.107 | 2.6461 | 2.651 | 0.24942 | 1 |  |  | 50 | 0
|  | #3L-13 ～#3L-14 | [9 empty] | Lighting | 1.08 | 1 | 0.9 | 1.2 | 0.9 | 5.3281 | 16.1761 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray |  | 97.7826 | 12.0898 |  |  |  | 0 | 0 | 0 | 2 | 0.626 | 12.2712 | 5.7157 |  |  | 5.7157 | 97.8457 | 1 | 0
[12 empty] | Wall socket | 2.19 | 1 | 0.6 | 3.65 | 0.4 | 7.2028 | [11 empty] | 96.4801 | 25.6932 |  |  |  | 0 | 0 | 0 | 2 | 0.0939 | 10.5557 | 5.0341 |  |  | 5.0341 |  | 3 | 0
[19 empty] | 12.2581 | 0.75779 | 38 | 1 | 2 |  | 14 | 1 | 4 |  |  | 3.5199 |  |  |  |  | 0 |  | 12.2581 | 12.2581 | 1.71 | 5.7133 | 5.7157 |  | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 10.5548 |  | 2.3882 |  | 0.3756 |  | 13.0476 |  | 0.856 |  | 97.8457 | 12.2581 | 10.5548 |  |  |  | 0 |  | 10.5548 | 10.5548 | 0.107 | 5.0337 | 5.0341 |  | 1 |  |  | 50 | 0
|  | #3L-14 ～#3L-15 | [9 empty] | Lighting | 1.08 | 1 | 0.9 | 1.2 | 0.9 | 5.3281 | 14.3662 | [5 empty] | 600V CV-T |  |  | Cable -tray |  | 97.7758 | 13.6119 |  |  |  | 0 | 0 | 0 | 2 |  | 10.6863 | 10.6863 |  |  | 10.6863 | 97.8457 | 1 | 0
[12 empty] | Wall socket | 2.67 | 1 | 0.6 | 4.45 | 0.4 | 8.7815 | [11 empty] | 96.4734 | 13.6119 |  |  |  | 0 | 0 | 0 | 2 |  | 9.617 | 9.617 |  |  | 9.617 |  | 3 | 0
[19 empty] | 10.6732 | 0.74294 |  |  |  |  | 14 | 1 | 4 |  |  | 3.5266 |  |  |  |  | 0 |  | 10.6732 | 10.6732 | 1.71 | 10.6863 | 10.6863 |  | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 9.6161 | [5 empty] | 13.0476 |  | 0.856 |  | 97.8457 | 10.6732 | 9.6161 |  |  |  | 0 |  | 9.6161 | 9.6161 | 0.107 | 9.617 | 9.617 |  | 1 |  |  | 50 | 0
| 81L1 -03 | No.8 Substation TR No8-1 #3S-1 ～#3L-K1 | [9 empty] | Lighting | 1.755 | 1 | 0.9 | 1.95 | 0.9 | 8.6581 | 11.1197 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray | 98.5188 | 98.0917 | 17.6429 | MCCB-3P |  |  | 0 | 0 | 0 | 2 | 0.626 | 8.6054 | 0.25575 | 0.28489 |  | 0.25575 | 98.1854 | 1 | 0
[12 empty] | Wall socket | 2.91 | 1 | 0.6 | 4.85 | 0.4 | 9.5708 | [11 empty] | 96.7851 | 523.1783 |  |  |  | 0 | 0 | 0 | 2 | 0.0939 | 7.0591 | 0.27473 | 0.3094 |  | 0.27473 |  | 3 | 0
[19 empty] | 8.5924 | 0.77272 | 38 | 1 | 12 |  | 14 | 1 | 4 |  |  | 3.2149 |  | 100 | 75 |  | 0 |  | 8.5924 | 8.5924 | 1.71 | 2.4732 | 2.4875 | 0.25575 | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 7.0582 |  | 14.3294 |  | 2.2536 |  | 13.0476 |  | 0.856 |  |  | 8.5924 | 7.0582 |  |  |  | 0 |  | 7.0582 | 7.0582 | 0.107 | 2.439 | 2.4413 | 0.27473 | 1 |  |  | 50 | 0
Drop down LIST |  | #3L-K1 ～#3L-17 | [9 empty] | Lighting | 0.54 | 1 | 0.9 | 0.6 | 0.9 | 2.664 | 11.3501 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray |  | 98.0681 | 17.2806 |  |  |  | 0 | 0 | 0 | 2 | 0.626 | 7.5321 | 3.4362 |  |  | 3.4362 | 98.1483 | 1 | 0
construction of cable | [11 empty] | Wall socket | 4.62 | 1 | 0.6 | 7.7 | 0.4 | 15.1949 | [11 empty] | 96.7618 | 38.9827 |  |  |  | 0 | 0 | 0 | 2 | 0.0939 | 8.5031 | 3.6809 |  |  | 3.6809 |  | 3 | 0
[19 empty] | 7.5191 | 0.66247 | 38 | 1 | 2 |  | 14 | 1 | 4 |  |  | 3.2382 |  |  |  |  | 0 |  | 7.5191 | 7.5191 | 1.71 | 3.4338 | 3.4362 |  | 0 |  | 197.0377 | 202.7 | 0
Cabletray |  |  | 75 | [15 empty] | 8.5022 |  | 2.3882 |  | 0.3756 |  | 13.0476 |  | 0.856 |  | 98.1483 | 7.5191 | 8.5022 |  |  |  | 0 |  | 8.5022 | 8.5022 | 0.107 | 3.6805 | 3.6809 |  | 1 |  |  | 50 | 0
Subter- ranean |  | #3L-17 ～#3L-16 | [9 empty] | Lighting | 1.08 | 1 | 0.9 | 1.2 | 0.9 | 5.3281 | 9.0104 | [5 empty] | 600V CV-T |  |  | Cable -tray |  | 97.8849 | 21.7272 |  |  |  | 0 | 0 | 0 | 2 |  | 6.2975 | 6.2975 |  |  | 6.2975 | 98.1483 | 1 | 0
Under drain | [11 empty] | Wall socket | 5.22 | 1 | 0.6 | 8.7 | 0.4 | 17.1682 | [11 empty] | 96.5811 | 21.7272 |  |  |  | 0 | 0 | 0 | 2 |  | 6.4781 | 6.4781 |  |  | 6.4781 |  | 3 | 0
Openpit | [18 empty] | 6.2649 | 0.69529 |  |  |  |  | 14 | 1 | 10 |  |  | 3.4189 |  |  |  |  | 0 |  | 6.2649 | 6.2649 | 1.71 | 6.2975 | 6.2975 |  | 0 |  | 197.0377 | 202.7 | 0
Exposure piping |  |  | 75 | [15 empty] | 6.476 | [5 empty] | 32.6189 |  | 2.14 |  | 98.1483 | 6.2649 | 6.476 |  |  |  | 0 |  | 6.476 | 6.476 | 0.107 | 6.4781 | 6.4781 |  | 1 |  |  | 50 | 0
Conceal. piping | 81L1 -04 | No.8 Substation TR No8-1 #3S-1 ～#3L-18 | [9 empty] | Lighting | 1.35 | 1 | 0.9 | 1.5 | 0.9 | 6.6601 | 7.5114 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray | 98.5188 | 97.6747 | 26.0071 | MCCB-3P |  |  | 0 | 0 | 0 | 2 | 0.626 | 5.2657 | 0.28489 | 0.32584 |  | 0.28489 | 97.833 | 1 | 0
[12 empty] | Wall socket | 6.18 | 1 | 0.6 | 10.3 | 0.4 | 20.3256 | [11 empty] | 96.3737 | 465.2247 |  |  |  | 0 | 0 | 0 | 2 | 0.0939 | 5.3736 | 0.3094 | 0.35535 |  | 0.3094 |  | 3 | 0
[19 empty] | 5.2494 | 0.69886 | 38 | 1 | 24 |  | 14 | 1 | 5 |  |  | 3.6263 |  | 100 | 100 |  | 0 |  | 5.2494 | 5.2494 | 1.71 | 2.2369 | 2.2656 | 0.28489 | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 5.3726 |  | 28.6588 |  | 4.5072 |  | 16.3094 |  | 1.07 |  |  | 5.2494 | 5.3726 |  |  |  | 0 |  | 5.3726 | 5.3726 | 0.107 | 2.387 | 2.3915 | 0.3094 | 1 |  |  | 50 | 0
|  | #3L-18 ～#3L-19 | [9 empty] | Lighting | 1.17 | 1 | 0.9 | 1.3 | 0.9 | 5.7721 | 5.7626 | [5 empty] | 600V CV-T |  |  | Cable -tray |  | 97.4367 | 33.817 |  |  |  | 0 | 0 | 0 | 2 |  | 3.8834 | 3.8834 |  |  | 3.8834 | 97.833 | 1 | 0
[12 empty] | Wall socket | 8.94 | 1 | 0.6 | 14.9 | 0.4 | 29.4031 | [11 empty] | 96.1389 | 33.817 |  |  |  | 0 | 0 | 0 | 2 |  | 4.2892 | 4.2892 |  |  | 4.2892 |  | 3 | 0
[19 empty] | 3.8508 | 0.66824 |  |  |  |  | 14 | 1 | 10 |  |  | 3.8611 |  |  |  |  | 0 |  | 3.8508 | 3.8508 | 1.71 | 3.8834 | 3.8834 |  | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 4.287 | [5 empty] | 32.6189 |  | 2.14 |  | 97.833 | 3.8508 | 4.287 |  |  |  | 0 |  | 4.287 | 4.287 | 0.107 | 4.2892 | 4.2892 |  | 1 |  |  | 50 | 0
| 81L1 -05 | No.8 Substation TR No8-1 #3S-1 ～#3L-27 | [9 empty] | Lighting | 0.72 | 1 | 0.9 | 0.8 | 0.9 | 3.552 | 12.2284 | [5 empty] | 600V CV-T |  |  | Cable -tray | 98.5188 | 98.0567 | 16.0376 | MCCB-3P |  |  | 0 | 0 | 0 | 2 |  | 8.4804 | 0.32584 |  |  | 0.32584 | 98.5188 | 1 | 0
[12 empty] | Wall socket | 3.96 | 1 | 0.6 | 6.6 | 0.4 | 13.0242 | [11 empty] | 96.7505 | 408.6804 |  |  |  | 0 | 0 | 0 | 2 |  | 8.8898 | 0.35535 |  |  | 0.35535 |  | 3 | 0
[19 empty] | 8.4021 | 0.6871 |  |  |  |  | 14 | 1 | 24 |  |  | 3.2495 |  | 50 | 50 |  | 0 |  | 8.4021 | 8.4021 | 1.71 | 0.32584 | 0.32584 |  | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 8.8847 | [5 empty] | 78.2853 |  | 5.136 |  |  | 8.4021 | 8.8847 |  |  |  | 0 |  | 8.8847 | 8.8847 | 0.107 | 0.35535 | 0.35535 |  | 1 |  |  | 50 | 0
| 81L2 -01 | No.8 Substation TR No8-1 #3S-1 ～#3L-31 | [9 empty] | Lighting | 0.72 | 1 | 0.9 | 0.8 | 0.9 | 3.552 | 6.9404 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray | 98.5188 | 97.7715 | 28.1745 | MCCB-3P |  |  | 0 | 0 | 0 | 2 | 0.626 | 4.5354 | 0.33885 | 0.37294 |  | 0.33885 | 97.9005 | 1 | 0
[12 empty] | Wall socket | 7.8 | 1 | 0.6 | 13 | 0.4 | 25.6537 | [11 empty] | 96.4692 | 390.1819 |  |  |  | 0 | 0 | 0 | 2 | 0.0939 | 5.2656 | 0.37014 | 0.40802 |  | 0.37014 |  | 3 | 0
[19 empty] | 4.5223 | 0.65159 | 38 | 1 | 36 |  | 14 | 1 | 4 |  |  | 3.5308 |  | 100 | 75 |  | 0 |  | 4.5223 | 4.5223 | 1.71 | 3.6634 | 3.7064 | 0.33885 | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 5.2648 |  | 42.9882 |  | 6.7608 |  | 13.0476 |  | 0.856 |  |  | 4.5223 | 5.2648 |  |  |  | 0 |  | 5.2648 | 5.2648 | 0.107 | 3.979 | 3.9857 | 0.37014 | 1 |  |  | 50 | 0
|  | #3L-31 ～#3L-21 | [9 empty] | Lighting | 0.72 | 1 | 0.9 | 0.8 | 0.9 | 3.552 | 24.169 | [5 empty] | 600V CV-T |  |  | Cable -tray |  | 97.8477 | 8.097 |  |  |  | 0 | 0 | 0 | 2 |  | 18.319 | 18.319 |  |  | 18.319 | 97.9005 | 1 | 0
[12 empty] | Wall socket | 1.47 | 1 | 0.6 | 2.45 | 0.4 | 4.8347 | [11 empty] | 96.5444 | 8.097 |  |  |  | 0 | 0 | 0 | 2 |  | 15.7856 | 15.7856 |  |  | 15.7856 |  | 3 | 0
[19 empty] | 18.3027 | 0.75728 |  |  |  |  | 14 | 1 | 5 |  |  | 3.4556 |  |  |  |  | 0 |  | 18.3027 | 18.3027 | 1.71 | 18.319 | 18.319 |  | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 15.7845 | [5 empty] | 16.3094 |  | 1.07 |  | 97.9005 | 18.3027 | 15.7845 |  |  |  | 0 |  | 15.7845 | 15.7845 | 0.107 | 15.7856 | 15.7856 |  | 1 |  |  | 50 | 0
| 81L2 -02 | No.8 Substation TR No8-1 #3S-1 ～#3L-22 | [9 empty] | Lighting | 1.08 | 1 | 0.9 | 1.2 | 0.9 | 5.3281 | 4.325 | [5 empty] | 600V CV-T |  |  | Cable -tray | 98.5188 | 97.9767 | 45.3074 | MCCB-3P |  |  | 0 | 0 | 0 | 2 |  | 2.8331 | 0.37294 |  |  | 0.37294 | 98.5188 | 1 | 0
[12 empty] | Wall socket | 12.63 | 1 | 0.6 | 21.05 | 0.4 | 41.5392 | [11 empty] | 96.6717 | 356.4451 |  |  |  | 0 | 0 | 0 | 2 |  | 3.2995 | 0.40802 |  |  | 0.40802 |  | 3 | 0
[19 empty] | 2.8043 | 0.64841 |  |  |  |  | 60 | 1 | 38 |  |  | 3.3283 |  | 100 | 75 |  | 0 |  | 2.8043 | 2.8043 | 0.397 | 0.37294 | 0.37294 |  | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 3.2926 | [5 empty] | 28.7771 |  | 6.878 |  |  | 2.8043 | 3.2926 |  |  |  | 0 |  | 3.2926 | 3.2926 | 0.0905 | 0.40802 | 0.40802 |  | 1 |  |  | 50 | 0
| 81L2 -03 | No.8 Substation TR No8-1 #3S-1 ～#3L-23 | [9 empty] | Lighting | 1.71 | 1 | 0.9 | 1.9 | 0.9 | 8.4361 | 4.5703 | [5 empty] | 600V CV-T |  |  | Cable -tray | 98.5188 | 97.9288 | 42.8541 | MCCB-3P |  |  | 0 | 0 | 0 | 2 |  | 3.1341 | 0.42932 |  |  | 0.42932 | 98.5188 | 1 | 0
[12 empty] | Wall socket | 10.92 | 1 | 0.6 | 18.2 | 0.4 | 35.9151 | [11 empty] | 96.6244 | 311.1627 |  |  |  | 0 | 0 | 0 | 2 |  | 3.3642 | 0.46547 |  |  | 0.46547 |  | 3 | 0
[19 empty] | 3.0994 | 0.67816 |  |  |  |  | 38 | 1 | 29 |  |  | 3.3756 |  | 100 | 75 |  | 0 |  | 3.0994 | 3.0994 | 0.626 | 0.42932 | 0.42932 |  | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 3.3588 | [5 empty] | 34.6294 |  | 5.4462 |  |  | 3.0994 | 3.3588 |  |  |  | 0 |  | 3.3588 | 3.3588 | 0.0939 | 0.46547 | 0.46547 |  | 1 |  |  | 50 | 0
| 81L2 -04 | No.8 Substation TR No8-1 #3S-1 ～#3L-30 | [9 empty] | Lighting | 0.9 | 1 | 0.9 | 1 | 0.9 | 4.4401 | 3.1364 | [5 empty] | 600V CV-T |  |  | Cable -tray | 98.5188 | 97.7328 | 62.321 | MCCB-3P |  |  | 0 | 0 | 0 | 2 |  | 2.009 | 0.49747 |  |  | 0.49747 | 98.5188 | 1 | 0
[12 empty] | Wall socket | 18.3 | 1 | 0.6 | 30.5 | 0.4 | 60.1875 | [11 empty] | 96.431 | 268.3092 |  |  |  | 0 | 0 | 0 | 2 |  | 2.4413 | 0.54021 |  |  | 0.54021 |  | 3 | 0
[19 empty] | 1.9756 | 0.62989 |  |  |  |  | 38 | 1 | 28 |  |  | 3.569 |  | 100 | 100 |  | 0 |  | 1.9756 | 1.9756 | 0.626 | 0.49747 | 0.49747 |  | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 2.436 | [5 empty] | 33.4353 |  | 5.2584 |  |  | 1.9756 | 2.436 |  |  |  | 0 |  | 2.436 | 2.436 | 0.0939 | 0.54021 | 0.54021 |  | 1 |  |  | 50 | 0
| 81L3 -01 | No.8 Substation TR No8-1 #3S-1 ～#3L-29 | [9 empty] | Lighting | 0.72 | 1 | 0.9 | 0.8 | 0.9 | 3.552 | 12.3757 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray | 98.5188 | 98.1121 | 15.8556 | MCCB-3P |  |  | 0 | 0 | 0 | 2 | 0.626 | 8.5281 | 0.65931 | 0.83452 |  | 0.65931 | 98.1883 | 1 | 0
[12 empty] | Wall socket | 3.9 | 1 | 0.6 | 6.5 | 0.4 | 12.8268 | [11 empty] | 96.8053 | 205.4222 |  |  |  | 0 | 0 | 0 | 2 | 0.0939 | 8.9815 | 0.69223 | 0.87521 |  | 0.69223 |  | 3 | 0
[19 empty] | 8.515 | 0.68804 | 38 | 1 | 16 |  | 14 | 1 | 4 |  |  | 3.1947 |  | 100 | 75 |  | 0 |  | 8.515 | 8.515 | 1.71 | 3.1213 | 3.1404 | 0.65931 | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 8.9807 |  | 19.1059 |  | 3.0048 |  | 13.0476 |  | 0.856 |  |  | 8.515 | 8.9807 |  |  |  | 0 |  | 8.9807 | 8.9807 | 0.107 | 3.3079 | 3.3109 | 0.69223 | 1 |  |  | 50 | 0
|  | #3L-29 ～#3L-24 | [9 empty] | Lighting | 1.17 | 1 | 0.9 | 1.3 | 0.9 | 5.7721 | 7.1706 | [5 empty] | 600V CV-T |  |  | Cable -tray |  | 97.9599 | 27.3228 |  |  |  | 0 | 0 | 0 | 2 |  | 4.923 | 4.923 |  |  | 4.923 | 98.1883 | 1 | 0
[12 empty] | Wall socket | 6.84 | 1 | 0.6 | 11.4 | 0.4 | 22.4963 | [11 empty] | 96.6551 | 27.3228 |  |  |  | 0 | 0 | 0 | 2 |  | 5.2365 | 5.2365 |  |  | 5.2365 |  | 3 | 0
[19 empty] | 4.9002 | 0.68337 |  |  |  |  | 14 | 1 | 7 |  |  | 3.3449 |  |  |  |  | 0 |  | 4.9002 | 4.9002 | 1.71 | 4.923 | 4.923 |  | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 5.235 | [5 empty] | 22.8332 |  | 1.498 |  | 98.1883 | 4.9002 | 5.235 |  |  |  | 0 |  | 5.235 | 5.235 | 0.107 | 5.2365 | 5.2365 |  | 1 |  |  | 50 | 0
| 81L3 -02 | No.8 Substation TR No8-1 #3S-1 ～#3L-28 | [9 empty] | Lighting | 0.54 | 1 | 0.9 | 0.6 | 0.9 | 2.664 | 8.5957 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray | 98.5188 | 98.0151 | 22.8057 | MCCB-3P |  |  | 0 | 0 | 0 | 2 | 0.626 | 5.5906 | 0.83452 | 1.2143 |  | 0.83452 | 98.1711 | 1 | 0
[12 empty] | Wall socket | 6.36 | 1 | 0.6 | 10.6 | 0.4 | 20.9176 | [11 empty] | 96.7096 | 162.3605 |  |  |  | 0 | 0 | 0 | 2 | 0.0939 | 6.5472 | 0.87521 | 1.2413 |  | 0.87521 |  | 3 | 0
[19 empty] | 5.571 | 0.64812 | 38 | 1 | 15 |  | 14 | 1 | 6 |  |  | 3.2904 |  | 100 | 100 |  | 0 |  | 5.571 | 5.571 | 1.71 | 2.6436 | 2.6616 | 0.83452 | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 6.5459 |  | 17.9118 |  | 2.817 |  | 19.5713 |  | 1.284 |  |  | 5.571 | 6.5459 |  |  |  | 0 |  | 6.5459 | 6.5459 | 0.107 | 2.9576 | 2.9605 | 0.87521 | 1 |  |  | 50 | 0
|  | #3L-28 ～#3L-25 | [9 empty] | Lighting | 1.08 | 1 | 0.9 | 1.2 | 0.9 | 5.3281 | 7.337 | [5 empty] | 600V CV-T |  |  | Cable -tray |  | 97.9491 | 26.7 |  |  |  | 0 | 0 | 0 | 2 |  | 5.0058 | 5.0058 |  |  | 5.0058 | 98.1711 | 1 | 0
[12 empty] | Wall socket | 6.78 | 1 | 0.6 | 11.3 | 0.4 | 22.299 | [11 empty] | 96.6444 | 26.7 |  |  |  | 0 | 0 | 0 | 2 |  | 5.3868 | 5.3868 |  |  | 5.3868 |  | 3 | 0
[19 empty] | 4.983 | 0.67915 |  |  |  |  | 14 | 1 | 7 |  |  | 3.3556 |  |  |  |  | 0 |  | 4.983 | 4.983 | 1.71 | 5.0058 | 5.0058 |  | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 5.3853 | [5 empty] | 22.8332 |  | 1.498 |  | 98.1711 | 4.983 | 5.3853 |  |  |  | 0 |  | 5.3853 | 5.3853 | 0.107 | 5.3868 | 5.3868 |  | 1 |  |  | 50 | 0
| 81L3 -03 | No.8 Substation TR No8-1 #3S-1 ～#3L-26 | [9 empty] | Lighting | 0.81 | 1 | 0.9 | 0.9 | 0.9 | 3.9961 | 2.82 | [5 empty] | 600V CV-T |  |  | Cable -tray | 98.5188 | 97.9206 | 69.4474 | MCCB-3P |  |  | 0 | 0 | 0 | 2 |  | 1.7818 | 1.2143 |  |  | 1.2143 | 98.5188 | 1 | 0
[12 empty] | Wall socket | 20.64 | 1 | 0.6 | 34.4 | 0.4 | 67.8836 | [11 empty] | 96.6163 | 113.4714 |  |  |  | 0 | 0 | 0 | 2 |  | 2.2079 | 1.2413 |  |  | 1.2413 |  | 3 | 0
[19 empty] | 1.7606 | 0.62434 |  |  |  |  | 60 | 1 | 28 |  |  | 3.3837 |  | 100 | 100 |  | 0 |  | 1.7606 | 1.7606 | 0.397 | 1.2143 | 1.2143 |  | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 2.2028 | [5 empty] | 21.2042 |  | 5.068 |  |  | 1.7606 | 2.2028 |  |  |  | 0 |  | 2.2028 | 2.2028 | 0.0905 | 1.2413 | 1.2413 |  | 1 |  |  | 50 | 0
| 81L3 -04 | No.8 Substation TR No8-1 #3S-1 ～#3L-K2 | [9 empty] | Lighting | 1.467 | 1 | 0.9 | 1.63 | 0.9 | 7.2373 | 14.4318 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray | 98.5188 | 98.4454 | 13.5933 | MCCB-3P |  |  | 0 | 0 | 0 | 2 | 0.626 | 11.333 | 3.5034 |  |  | 3.5034 | 98.1609 | 1 | 0
[12 empty] | Wall socket | 2.07 | 1 | 0.6 | 3.45 | 0.4 | 6.8081 | [11 empty] | 97.1341 | 44.6673 |  |  |  | 0 | 0 | 0 | 2 | 0.0939 | 8.9527 | 2.6541 |  |  | 2.6541 |  | 3 | 0
[19 empty] | 11.3199 | 0.78437 | 38 | 1 | 15 |  | 14 | 1 | 4 |  |  | 2.8659 |  | 100 | 75 |  | 0 |  | 11.3199 | 11.3199 | 1.71 | 3.4855 | 3.5034 |  | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 8.9519 |  | 17.9118 |  | 2.817 |  | 13.0476 |  | 0.856 |  |  | 11.3199 | 8.9519 |  |  |  | 0 |  | 8.9519 | 8.9519 | 0.107 | 2.6512 | 2.6541 |  | 1 |  |  | 50 | 0
|  | #3L-K2 ～#3L-K3 | [9 empty] | Lighting | 3.69 | 1 | 0.9 | 4.1 | 0.9 | 18.2042 | 6.2159 | [5 empty] | 600V CV-T |  |  | Cable -tray |  | 97.0934 | 31.2402 |  |  |  | 0 | 0 | 0 | 2 |  | 5.0319 | 5.0319 |  |  | 5.0319 | 98.1609 | 1 | 0
[12 empty] | Wall socket | 4.38 | 1 | 0.6 | 7.3 | 0.4 | 14.4055 | [11 empty] | 95.8001 |  |  |  |  | 0 | 0 | 0 | 2 |  | 3.7646 | 3.7646 |  |  | 3.7646 |  | 3 | 0
[19 empty] | 4.9503 | 0.79639 |  |  |  |  | 14 | 1 | 25 |  |  | 4.1999 |  |  |  |  | 0 |  | 4.9503 | 4.9503 | 1.71 | 5.0319 | 5.0319 |  | 0 |  | 197.0377 | 202.7 | 0
|  |  | 75 | [15 empty] | 3.7593 | [5 empty] | 81.5472 |  | 5.35 |  | 98.1609 | 4.9503 | 3.7593 |  |  |  | 0 |  | 3.7593 | 3.7593 | 0.107 | 3.7646 | 3.7646 |  | 1 |  |  | 50 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 2 |  |  | 0 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 3 |  |  | 0 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 4 |  |  | 0 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 5 |  |  | 0 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 6 |  |  | 0 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 7 |  |  | 0 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 8 |  |  | 0 | 0
|  | TGCRDL Relocation Project | [13 empty] | ESE-VD4 Exchange circuit analysis calculation | [5 empty] | Co.,Ltd. Yoshimura Airchitecture Design Office | [6 empty] | K,Yoshimura |  | K,Sakai |  |  | Terminal voltage -07 (Standard)
Note on B12: Drop down LIST An addition, change, and deletion can do this registration cell.
Note on B46: Drop down LIST An addition, change, and deletion can do this registration cell.
Note on C8: Printing range
Note on F13: Please input the temperature of conductor for calculation. (Each line) -100[℃] ～ +300[℃] Attention: It calculates by 0[℃] if it does not input. Ａｂｏｕｔ ｔｈｅ ｔｅｍｐｅｒａｔｕｒｅ ｏｆ ｃｏｎｄｕｃｔｏｒ The degree 20[℃] is standard temperature. Generally, this temperature is 50-60 [℃] except for a cold district. Please decide on reference by carrying out the maximum per- mission temperature of a conductor.
Note on L3: It can use for the power transmission voltage at the time of regular of an independent trunk and a branch trunk, received voltage, load current, the check of power factor, the determination of series capacitor capacity, etc. Comment ■ is the object for cells which needs an input． ■ is an explanatory note etc. Input cell ■ should input a required matter. Calculation cell ■ is an automatic calculation cell, an input is impossible.
Note on L11: ↓Please choose out of a drop down list. When Liszt does not have [except oil cooled type and (F)-molded type], please perform after inputting data into the "transformer USER" of DATA Table.
Note on L13: Following transformer data is registered into DATA Table. （50/60Hz） ３φ３Ｗ－２０ ～ １０００［ＫＶＡ］ １φ３Ｗ－１０ ～ ５００［ＫＶＡ］ An exact value will be calculated if the change correction of the %R and %X of an adoption transformer is made by DATA Table. Calculation of transformer rated current is depended below. In the case of ３φ：TRcap／(√3 x Es) In the case of １φ：TRcap／ Es TRcap：Capacity of TR. Es：Secondary voltage of TR.
Note on M11: When a transformer is parallel operation, please input the number of a parallel transformer.
Note on N6: High-voltage Capacitor［Nichicon Corp.1991.5］ 3300V，6600V-50Hz，60Hz（no Series reactor） 50, 75,100,150,200,250,300 [KVar] 3300V，6600V-50Hz，60Hz（Series reactor 6％） 50, 75,100,150,200,250,300,400,500,600, 700,750,800,900,1000[KVar] 3300V，6600V-50Hz，60Hz（Series reactor 13％） 50, 75,100,150,200,250,300,400,500[KVar]
Note on N7: Low-voltage Capacitor［Nichicon Corp.1991.5］ 200V，220V-50Hz，60Hz（no Series reactor） 10, 15, 20, 25, 30, 50[KVar] 200V，220V-50Hz，60Hz（Series reactor ６％） 10, 15, 20, 25, 30, 40, 50, 75,100[KVar] 400，415，440，460V-50Hz，60Hz（no Series reactor） 10, 15, 20, 25, 30, 50, 75,100,150[KVar] 400，415，440，460V-50Hz，60Hz（Series reactor 6％） 10, 15, 20, 25, 30, 50, 75,100,150,200 250,300[KVar]
Note on N10: Ｓｅｒｉｅｓ ｐｏｗｅｒ ｃａｐａｃｉｔｏｒ When average power factor of total load is bad (delay), SC improves power factor, and it installs the electric power transfor- mer by the side of power distribution in order to operate efficiently.
Note on O10: When you perform accumulation calculation, be careful of the following point. Trunk branch etc., when you accumulate the voltage drop value of each section, please use four lines each of a "cell" continuously. When you move to independent trunk calculation or next another calculation, four or more lines should vacate and please be sure to input a cell.
Note on O11: Please choose out of a drop down list.
Note on Q11: In the case of induction motor load, please input in the range of ０＜～１．０００ In the case of other loads, please input ”１”
Note on R11: Please input the value of the range of ０＜～１．０００
Note on S11: Iｎｐｕｔ ＫＶＡ Input ＫＶＡ＝Output ＫＷ／（ｃｏｓφｘη） cosφ ：Power factor of Load η ：Efficiency of Load
Note on W10: Load side Series Power Capacitor SC improves delay power factor of induc- tive load, reduces voltage drop of a trunk, and it installs it in order to prevent the fall of primary voltage.
Note on X11: Please choose out of a drop down list. In inputting the size which is not in a data table, please register R and X (50Hz) of the cable into a data table.
Note on Z11: Please input the fruit length meter of a cable.
Note on AA10: Please choose out of a drop down list.
Note on AB11: Please choose out of a drop down list. In inputting the size which is not in a data table, please register R and X (50Hz) of the cable into a data table.
Note on AD11: Please input the fruit length meter of a cable.
Note on AE10: Please choose out of a drop down list.
Note on AF10: Secondary transformer side voltage ［Ｖ］
Note on AF13: Voltage of the circuit diagram EB section ［Ｖ］
Note on AG11: Percent to power supply voltage [％]
Note on AG12: Percent of line voltage drop to power supply voltage [％]
Note on AJ11: ↓Please choose out of a drop down list. The important matter about selection of the frame / trip value of MCCB １） The check of interception capacity ２） The characteristic and the temperature conditions of MCCB ３） Grasp of the real load current which took into consideration the demand factor, load factor, divercity factor,voltage regulation rate of transformer, unbalance factor, etc. at the time of regular operation of a motor, at the time of starting of a motor. Frame value [A] of MCCB（Ｍｏｌｄｅｄ ｃａｓｅ ｃｉｒｃｕｉｔ ｂｒｅａｋｅｒ） ３０， ５０， ６０， １００， ２２５， ２５０， ４００， ６００， ８００，１０００， １２００，１６００，２０００，２５００，３０００， ３２００，４０００ Frame value [A] of ＡＣＢ（Ａｉｒ ｃｉｒｃｕｉｔ ｂｒｅａｋｅｒ） ６３０，１０００，１２５０，１６００，２０００， ２５００，３２００，４０００，５０００，６３００
Note on AJ12: Please choose out of a drop down list.
Note on AJ13: Please choose out of a drop down list.
Approved
Checked
Input cell
Exchange circuit analisys calculation -VD４
２００２ Ａｕｇ． Ｖｅｒ ２．0 by ＥＳＥ SERVICE
Automatic display
A "comment" will be displayed if cursor is brought close to the cell of upper right red.

## 3S-1(P)
⇒
0.15221
High volt. Capacitor
2002/08/01 Ver1.4
| Trunk number | Application section | Electric system | [5 empty] | Distribution side apparatus |  |  | Load side apparatus | [8 empty] | Selection-1 (Branch trunk) |  |  |  | Selection-2 (Trunk) |  |  |  | Transmission | Reception |  | Distribution |  | Note
|  |  | Sec. voltage ES[V] | [5 empty] | Power transformer |  | SCS Capacity | Load equipment capacity | [7 empty] | SCL Capacity | Cable name |  |  | Construct | Cable name |  |  | Construct | Voltage ER [V] | Voltage ＥＬ[V] | Current IL [A] | side |  |  | 1 phi-R | User-R | SCS | nphinW-1 | R-C1n | R-n2 | R-n4 |  |  | R-01 | E-Cn | Phi-G 20 | Load classification
|  |  | φ |  | W |  | V |  | Form | Number |  | Load classification | Output | Effici- ency | Power factor | Input | Demand factor | Load current | Ｚ Ｌ [Ω] |  | Cross | No. | Cable | Permission current[A] | Cross | No. | Cable | Permission current[A] | All load [A] | ＥＬ／Ｅ[％] | Current IC [A] | Breaker |  |  | 1 phi-X | User-X | SCLoad | nphinW-2 | X-C1n | X-n2 | X-n4 |  |  | X-01 |  | w-I20
Drop down LIST |  |  | Frequency [Hz] | [6 empty] | ％ Z | [Kvar] | [7 empty] | Ｒ Ｌ [Ω] | [Kvar] | section |  | span |  | section |  | span |  | TR current [A] | (Ｅ-ＥＬ)／Ｅ[％] | (Total) | Name |  |  | 3 phi-R | R-TR | R-n1 | R-n1' | R-C2n | R-n3 | R-n4' | R-n4' |  | R-02 | ES | E-K20
Load Classification |  |  | Calculation temp. | [5 empty] | Capacity/Rated current |  |  |  | [KW] | η | cosφ | [KVA] | Df | [A] | Ｘ Ｌ [Ω] | Avrg. PF | Ｚ Ｃ１ (Trunk) |  |  |  | Ｚ Ｃ２ (Branch trunk) |  |  |  | Branch part [V] | Zｎ１（Ｌｎ＋ＣＬ１） |  | -AF | -AT |  | 3 phi-X | X-TR | X-n1 | X-n1' | X-C2n | X-n3 | X-n4' | X-n4' |  | X-02 |  | Hz-G22
|  | No.8 Substation TR No.8-2 #3S-1 Secondary side | [33 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
Prod. power | [35 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
Experimental eq. | [37 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
AC M/C | [37 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
Supply fan | 82P1 -01 | No.8 Substation TR No8-2 #3S-1 ～#3P-11 | 3 | φ | 3 | W | 203.6 | V | (F)molded type | 1 |  | Test machine | 8.8 | 1 | 0.8 | 11 | 0.4 | 12.4771 | 7.0176 | [5 empty] | 600V CV-T |  |  | Cable -tray | 198.6006 | 197.792 | 28.1852 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 5.6461 | 0.15221 |  |  | 0.15221 | 198.6006 | 3 | 0
Exhaust fan | [9 empty] | 4.2276 |  | AC power | 5.9 | 0.8 | 0.8 | 9.2188 | 0.6 | 15.685 | [10 empty] | 1044.6356 | 97.1474 | 1044.6356 |  |  |  | 0 | 0 | 0 | 1 |  | 4.2156 | 0.11391 |  |  | 0.11391 |  | 3 | 0
|  |  | 50 | [5 empty] | 500 |  |  |  | 0.4 | 1 | 0.8 | 0.5 | 0.6 | 0.85071 | 5.6141 | 0.8 |  |  |  |  | 38 | 1 | 31 |  | 1044.6356 | 2.8526 |  | 100 | 100 |  | 1.07 | 0.0015365 | 5.6141 | 5.6141 | 0.626 | 0.15221 | 0.15221 |  | 0 | 0.15375 | 198.6006 | 203.6 | 0
sanitation |  |  | 75 | [5 empty] | 1417.8543 | [9 empty] | 4.2105 | [5 empty] | 32.0582 |  | 5.0418 |  |  | 5.6141 | 4.2105 |  |  |  | 4.09 | 0.0058731 | 4.2105 | 4.2105 | 0.0939 | 0.11391 | 0.11391 |  | 1 | 0.11978 |  | 50 | 0
Septic tank | 82P1 -02 | No.8 Substation TR No8-2 #3S-1 ～#3P-12 | [9 empty] | Test machine | 68.96 | 1 | 0.8 | 86.2 | 0.4 | 97.7752 | 2.0823 | [5 empty] | 600V CV-T |  |  | Cable -tray | 198.6006 | 198.2109 | 95.1872 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.6689 | 0.15643 |  |  | 0.15643 | 198.6006 | 3 | 0
[30 empty] | 97.3531 | 1016.4504 |  |  |  | 0 | 0 | 0 | 1 |  | 1.2521 | 0.11707 |  |  | 0.11707 |  | 3 | 0
[19 empty] | 1.6659 | 0.8 |  |  |  |  | 250 | 1 | 19 |  |  | 2.6469 |  | 400 | 350 |  | 0 |  | 1.6659 | 1.6659 | 0.0981 | 0.15643 | 0.15643 |  | 0 |  | 198.6006 | 203.6 | 0
Existing load |  |  | 75 | [15 empty] | 1.2494 | [5 empty] | 3.0791 |  | 2.7183 |  |  | 1.6659 | 1.2494 |  |  |  | 0 |  | 1.2494 | 1.2494 | 0.0826 | 0.11707 | 0.11707 |  | 1 |  |  | 50 | 0
| 82P1 -03 | No.8 Substation TR No8-2 #3S-1 ～#3P-13 | [9 empty] | Test machine | 1.9 | 0.8 | 0.8 | 2.9688 | 0.4 | 3.3674 | 3.7814 | [5 empty] | 600V CV-T |  |  | Cable -tray | 198.6006 | 197.9583 | 52.351 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 3.037 | 0.17261 |  |  | 0.17261 | 198.6006 | 3 | 0
[13 empty] | 35.6 | 1 | 0.8 | 44.5 | 0.4 | 50.4756 | [11 empty] | 97.229 | 921.2633 |  |  |  | 0 | 0 | 0 | 1 |  | 2.2734 | 0.12915 |  |  | 0.12915 |  | 3 | 0
Lighting Load | [18 empty] | 3.0251 | 0.8 |  |  |  |  | 100 | 1 | 30 |  |  | 2.771 |  | 225 | 175 |  | 0 |  | 3.0251 | 3.0251 | 0.24 | 0.17261 | 0.17261 |  | 0 |  | 198.6006 | 203.6 | 0
Wall socket |  |  | 75 | [15 empty] | 2.2688 | [5 empty] | 11.8942 |  | 4.5882 |  |  | 3.0251 | 2.2688 |  |  |  | 0 |  | 2.2688 | 2.2688 | 0.0883 | 0.12915 | 0.12915 |  | 1 |  |  | 50 | 0
| 82P2 -01 | No.8 Substation TR No8-2 #3S-1 ～#3P-14 | [9 empty] | Test machine | 60.4 | 1 | 0.8 | 75.5 | 0.4 | 85.6384 | 2.3774 | [5 empty] | 600V CV-T |  |  | Cable -tray | 198.6006 | 197.5132 | 83.0782 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.9146 | 0.18301 |  |  | 0.18301 | 198.6006 | 3 | 0
[30 empty] | 97.0104 | 868.9123 |  |  |  | 0 | 0 | 0 | 1 |  | 1.4314 | 0.13692 |  |  | 0.13692 |  | 3 | 0
[19 empty] | 1.902 | 0.8 |  |  |  |  | 100 | 1 | 32 |  |  | 2.9896 |  | 225 | 225 |  | 0 |  | 1.902 | 1.902 | 0.24 | 0.18301 | 0.18301 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 1.4265 | [5 empty] | 12.6872 |  | 4.8941 |  |  | 1.902 | 1.4265 |  |  |  | 0 |  | 1.4265 | 1.4265 | 0.0883 | 0.13692 | 0.13692 |  | 1 |  |  | 50 | 0
| 82P2 -02 | No.8 Substation TR No8-2 #3S-1 ～#3P-15 | [9 empty] | Test machine | 7.2 | 1 | 0.8 | 9 | 0.4 | 10.2086 | 19.9441 | [5 empty] | 600V CV-T |  |  | Cable -tray | 198.6006 | 198.3063 | 9.9431 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 15.9883 | 0.20235 |  |  | 0.20235 | 198.6006 | 3 | 0
[30 empty] | 97.3999 | 785.8341 |  |  |  | 0 | 0 | 0 | 1 |  | 11.9716 | 0.15141 |  |  | 0.15141 |  | 3 | 0
[19 empty] | 15.9553 | 0.8 |  |  |  |  | 38 | 1 | 32 |  |  | 2.6001 |  | 100 | 100 |  | 0 |  | 15.9553 | 15.9553 | 0.626 | 0.20235 | 0.20235 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 11.9664 | [5 empty] | 33.0924 |  | 5.2045 |  |  | 15.9553 | 11.9664 |  |  |  | 0 |  | 11.9664 | 11.9664 | 0.0939 | 0.15141 | 0.15141 |  | 1 |  |  | 50 | 0
| 82P2 -03 | No.8 Substation TR No8-2 #3S-1 ～#3P-16 | [9 empty] | Test machine | 3 | 0.8 | 0.8 | 4.6875 | 0.4 | 5.317 | 38.2926 | [5 empty] | 600V CV-T |  |  | Cable -tray | 198.6006 | 198.5493 | 5.1851 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 30.6446 | 0.20494 |  |  | 0.20494 | 198.6006 | 3 | 0
[13 empty] | 12 | 1 | 0.8 | 15 |  | 0 | [11 empty] | 97.5193 | 775.891 |  |  |  | 0 | 0 | 0 | 1 |  | 22.9781 | 0.15335 |  |  | 0.15335 |  | 3 | 0
[19 empty] | 30.6341 | 0.8 |  |  |  |  | 60 | 1 | 16 |  |  | 2.4807 |  | 100 | 100 |  | 0 |  | 30.6341 | 30.6341 | 0.397 | 0.20494 | 0.20494 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 22.9756 | [5 empty] | 10.4933 |  | 2.508 |  |  | 30.6341 | 22.9756 |  |  |  | 0 |  | 22.9756 | 22.9756 | 0.0905 | 0.15335 | 0.15335 |  | 1 |  |  | 50 | 0
Drop down LIST | 82P2 -04 | No.8 Substation TR No8-2 #3S-1 ～#3P-17 | [9 empty] | Test machine | 39.52 | 1 | 0.8 | 49.4 | 0.4 | 56.0336 | 3.6335 | [5 empty] | 600V CV-T |  |  | Cable -tray | 198.6006 | 197.9322 | 54.4738 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 2.9187 | 0.20632 |  |  | 0.20632 | 198.6006 | 3 | 0
construction of cable | [29 empty] | 97.2162 | 770.7059 |  |  |  | 0 | 0 | 0 | 1 |  | 2.1847 | 0.15438 |  |  | 0.15438 |  | 3 | 0
[19 empty] | 2.9068 | 0.8 |  |  |  |  | 100 | 1 | 30 |  |  | 2.7838 |  | 225 | 150 |  | 0 |  | 2.9068 | 2.9068 | 0.24 | 0.20632 | 0.20632 |  | 0 |  | 198.6006 | 203.6 | 0
Cabletray |  |  | 75 | [15 empty] | 2.1801 | [5 empty] | 11.8942 |  | 4.5882 |  |  | 2.9068 | 2.1801 |  |  |  | 0 |  | 2.1801 | 2.1801 | 0.0883 | 0.15438 | 0.15438 |  | 1 |  |  | 50 | 0
Subter- ranean | 82P2 -05 | No.8 Substation TR No8-2 #3S-1 ～#3P-18 | [9 empty] | Test machine | 1.5 | 0.8 | 0.8 | 2.3438 | 0.4 | 2.6585 | 63.1197 | [5 empty] | 600V CV-T |  |  | Cable -tray | 198.6006 | 198.4415 | 3.1439 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 50.5546 | 0.22202 |  |  | 0.22202 | 198.6006 | 3 | 0
Under drain | [12 empty] | 0.4 | 1 | 0.8 | 0.5 | 0.4 | 0.56714 | [11 empty] | 97.4664 | 716.2322 |  |  |  | 0 | 0 | 0 | 1 |  | 37.8776 | 0.16612 |  |  | 0.16612 |  | 3 | 0
Openpit | [18 empty] | 50.4957 | 0.8 |  |  |  |  | 22 | 1 | 33 |  |  | 2.5336 |  | 100 | 75 |  | 0 |  | 50.4957 | 50.4957 | 1.08 | 0.22202 | 0.22202 |  | 0 |  | 198.6006 | 203.6 | 0
Exposure piping |  |  | 75 | [15 empty] | 37.8718 | [5 empty] | 58.8764 |  | 5.8301 |  |  | 50.4957 | 37.8718 |  |  |  | 0 |  | 37.8718 | 37.8718 | 0.102 | 0.16612 | 0.16612 |  | 1 |  |  | 50 | 0
Conceal. piping | 82P2 -06 | No.8 Substation TR No8-2 #3S-1 ～Elevator control board | [9 empty] | Elevator | 2.944 | 0.8 | 0.8 | 4.6 | 0.05 | 0.65221 | 312.168 | [5 empty] | 600V CV-3C |  |  | Cable -tray | 198.6006 | 198.5644 | 0.63608 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 249.804 | 0.223 |  |  | 0.223 | 198.6006 | 3 | 0
[30 empty] | 97.5267 | 713.0883 |  |  |  | 0 | 0 | 0 | 1 |  | 187.3029 | 0.16685 |  |  | 0.16685 |  | 3 | 0
[19 empty] | 249.7344 | 0.8 |  |  |  |  | 8 | 1 | 14 |  |  | 2.4733 |  | 50 | 50 |  | 0 |  | 249.7344 | 249.7344 | 3.01 | 0.223 | 0.223 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 187.3008 | [5 empty] | 69.6142 |  | 2.1096 |  |  | 249.7344 | 187.3008 |  |  |  | 0 |  | 187.3008 | 187.3008 | 0.087 | 0.16685 | 0.16685 |  | 1 |  |  | 50 | 0
| 82P3 -01 | No.8 Substation TR No8-2 #3S-1 ～#3P-21 | [9 empty] | Test machine | 3 | 0.8 | 0.8 | 4.6875 | 0.4 | 5.317 | 11.8187 | [5 empty] | 600V CV-T |  |  | Cable -tray | 198.6006 | 197.9806 | 16.7515 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 9.4963 | 0.2232 |  |  | 0.2232 | 198.6006 | 3 | 0
[13 empty] | 8.4 | 1 | 0.8 | 10.5 | 0.4 | 11.91 | [11 empty] | 97.24 | 712.4522 |  |  |  | 0 | 0 | 0 | 1 |  | 7.0977 | 0.167 |  |  | 0.167 |  | 3 | 0
[19 empty] | 9.455 | 0.8 |  |  |  |  | 38 | 1 | 40 |  |  | 2.76 |  | 100 | 100 |  | 0 |  | 9.455 | 9.455 | 0.626 | 0.2232 | 0.2232 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 7.0912 | [5 empty] | 41.3655 |  | 6.5056 |  |  | 9.455 | 7.0912 |  |  |  | 0 |  | 7.0912 | 7.0912 | 0.0939 | 0.167 | 0.167 |  | 1 |  |  | 50 | 0
| 82P3 -02 | No.8 Substation TR No8-2 #3S-1 ～#3P-24 | [9 empty] | Test machine | 1.5 | 0.8 | 0.8 | 2.3438 | 0.4 | 2.6585 | 12.0924 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray | 198.6006 | 198.2241 | 16.3924 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 | 0.397 | 9.6781 | 0.22857 | 0.23775 |  | 0.22857 | 198.2847 | 3 | 0
[13 empty] | 10 | 1 | 0.8 | 12.5 | 0.4 | 14.1785 | [11 empty] | 97.3596 | 694.5941 |  |  |  | 0 | 0 | 0 | 1 | 0.0905 | 7.2561 | 0.17102 | 0.17789 |  | 0.17102 |  | 3 | 0
[19 empty] | 9.6739 | 0.8 | 60 | 1 | 19 |  | 38 | 1 | 4 |  |  | 2.6404 |  | 100 | 100 |  | 0 |  | 9.6739 | 9.6739 | 0.626 | 5.9056 | 5.918 | 0.22857 | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 7.2554 |  | 12.4608 |  | 2.9783 |  | 4.1365 |  | 0.65056 |  |  | 9.6739 | 7.2554 |  |  |  | 0 |  | 7.2554 | 7.2554 | 0.0939 | 4.4268 | 4.4298 | 0.17102 | 1 |  |  | 50 | 0
|  | #3P-24 ～#3P-23 | [9 empty] | Test machine | 1.5 | 0.8 | 0.8 | 2.3438 | 0.4 | 2.6585 | 27.0174 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray |  | 198.157 | 7.3344 |  |  |  | 0 | 0 | 0 | 1.7321 | 0.626 | 21.6252 | 15.1502 |  |  | 15.1502 | 198.2266 | 3 | 0
[13 empty] | 3.44 | 1 | 0.8 | 4.3 | 0.4 | 4.8774 | [11 empty] | 97.3266 | 10.4704 |  |  |  | 0 | 0 | 0 | 1 | 0.0939 | 16.2112 | 11.3531 |  |  | 11.3531 |  | 3 | 0
[19 empty] | 21.6139 | 0.8 | 38 | 1 | 6 |  | 14 | 1 | 4 |  |  | 2.6734 |  |  |  |  | 0 |  | 21.6139 | 21.6139 | 1.71 | 15.144 | 15.1502 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 16.2104 |  | 6.2048 |  | 0.97584 |  | 11.2995 |  | 0.74132 |  | 198.2266 | 21.6139 | 16.2104 |  |  |  | 0 |  | 16.2104 | 16.2104 | 0.107 | 11.3521 | 11.3531 |  | 1 |  |  | 50 | 0
|  | #3P-23 ～#3P-22 | [9 empty] | Test machine | 1.5 | 0.8 | 0.8 | 2.3438 | 0.4 | 2.6585 | 63.1197 | [5 empty] | 600V CV-T |  |  | Cable -tray |  | 198.1373 | 3.1391 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 50.5296 | 50.5296 |  |  | 50.5296 | 198.2266 | 3 | 0
[13 empty] | 0.4 | 1 | 0.8 | 0.5 | 0.4 | 0.56714 | [11 empty] | 97.3169 | 3.1391 |  |  |  | 0 | 0 | 0 | 1 |  | 37.874 | 37.874 |  |  | 37.874 |  | 3 | 0
[19 empty] | 50.4957 | 0.8 |  |  |  |  | 14 | 1 | 12 |  |  | 2.6831 |  |  |  |  | 0 |  | 50.4957 | 50.4957 | 1.71 | 50.5296 | 50.5296 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 37.8718 | [5 empty] | 33.8985 |  | 2.224 |  | 198.2266 | 50.4957 | 37.8718 |  |  |  | 0 |  | 37.8718 | 37.8718 | 0.107 | 37.874 | 37.874 |  | 1 |  |  | 50 | 0
| 82P3 -03 | No.8 Substation TR No8-2 #3S-1 ～#3P-25 | [9 empty] | Test machine | 1.5 | 0.8 | 0.8 | 2.3438 | 0.4 | 2.6585 | 16.553 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray | 198.6006 | 198.1893 | 11.973 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 | 0.626 | 13.2495 | 0.23775 | 0.24519 |  | 0.23775 | 198.2628 | 3 | 0
[13 empty] | 6.8 | 1 | 0.8 | 8.5 | 0.4 | 9.6414 | [11 empty] | 97.3425 | 667.6971 |  |  |  | 0 | 0 | 0 | 1 | 0.0939 | 9.9325 | 0.17789 | 0.18345 |  | 0.17789 |  | 3 | 0
[19 empty] | 13.2424 | 0.8 | 38 | 1 | 18 |  | 22 | 1 | 4 |  |  | 2.6575 |  | 100 | 100 |  | 0 |  | 13.2424 | 13.2424 | 1.08 | 7.822 | 7.8407 | 0.23775 | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 9.9318 |  | 18.6145 |  | 2.9275 |  | 7.1365 |  | 0.70668 |  |  | 13.2424 | 9.9318 |  |  |  | 0 |  | 9.9318 | 9.9318 | 0.102 | 5.8617 | 5.8646 | 0.17789 | 1 |  |  | 50 | 0
|  | #3P-25 ～#3P-26 | [9 empty] | Test machine | 4.5 | 0.8 | 0.8 | 7.0312 | 0.4 | 7.9754 | 23.8336 | [5 empty] | 600V CV-T |  |  | Cable -tray |  | 198.0657 | 8.3104 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 19.0951 | 19.0951 |  |  | 19.0951 | 198.2628 | 3 | 0
[13 empty] | 0.4 | 1 | 0.8 | 0.5 | 0.4 | 0.56714 | [11 empty] | 97.2818 | 8.3104 |  |  |  | 0 | 0 | 0 | 1 |  | 14.302 | 14.302 |  |  | 14.302 |  | 3 | 0
[19 empty] | 19.0669 | 0.8 |  |  |  |  | 14 | 1 | 10 |  |  | 2.7182 |  |  |  |  | 0 |  | 19.0669 | 19.0669 | 1.71 | 19.0951 | 19.0951 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 14.3001 | [5 empty] | 28.2488 |  | 1.8533 |  | 198.2628 | 19.0669 | 14.3001 |  |  |  | 0 |  | 14.3001 | 14.3001 | 0.107 | 14.302 | 14.302 |  | 1 |  |  | 50 | 0
| 82P3 -04 | No.8 Substation TR No8-1 #3S-1 ～#3L-27 | [9 empty] | Test machine | 3 | 0.8 | 0.8 | 4.6875 | 0.4 | 5.317 | 20.6615 | [5 empty] | 600V CV-T |  |  | Cable -tray | 198.6006 | 198.458 | 9.6052 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 16.5449 | 0.24519 |  |  | 0.24519 | 198.6006 | 3 | 0
[13 empty] | 3.2 | 1 | 0.8 | 4 | 0.4 | 4.5371 | [11 empty] | 97.4744 | 648.5514 |  |  |  | 0 | 0 | 0 | 1 |  | 12.4006 | 0.18345 |  |  | 0.18345 |  | 3 | 0
[19 empty] | 16.5292 | 0.8 |  |  |  |  | 60 | 1 | 24 |  |  | 2.5256 |  | 100 | 100 |  | 0 |  | 16.5292 | 16.5292 | 0.397 | 0.24519 | 0.24519 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 12.3969 | [5 empty] | 15.74 |  | 3.762 |  |  | 16.5292 | 12.3969 |  |  |  | 0 |  | 12.3969 | 12.3969 | 0.0905 | 0.18345 | 0.18345 |  | 1 |  |  | 50 | 0
| 82P3 -05 | No.8 Substation TR No8-1 #3S-1 ～#3L-28 | [9 empty] | Test machine | 3 | 0.8 | 0.8 | 4.6875 | 0.4 | 5.317 | 34.6018 | [5 empty] | 600V CV-T |  |  | Cable -tray | 198.6006 | 198.4574 | 5.7355 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 27.7093 | 0.24888 |  |  | 0.24888 | 198.6006 | 3 | 0
[13 empty] | 0.4 | 1 | 0.8 | 0.5 | 0.4 | 0.56714 | [11 empty] | 97.4742 | 638.9462 |  |  |  | 0 | 0 | 0 | 1 |  | 20.7654 | 0.18621 |  |  | 0.18621 |  | 3 | 0
[19 empty] | 27.6814 | 0.8 |  |  |  |  | 38 | 1 | 27 |  |  | 2.5258 |  | 50 | 50 |  | 0 |  | 27.6814 | 27.6814 | 0.626 | 0.24888 | 0.24888 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 20.7611 | [5 empty] | 27.9217 |  | 4.3913 |  |  | 27.6814 | 20.7611 |  |  |  | 0 |  | 20.7611 | 20.7611 | 0.0939 | 0.18621 | 0.18621 |  | 1 |  |  | 50 | 0
| 82P3 -06 | No.8 Substation TR No8-1 #3S-1 ～#3L-29 | [9 empty] | Test machine | 32.72 | 1 | 0.8 | 40.9 | 0.4 | 46.3922 | 4.3887 | [5 empty] | 600V CV-T |  |  | Cable -tray | 198.6006 | 198.1943 | 45.1604 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 3.5197 | 0.25113 |  |  | 0.25113 | 198.6006 | 3 | 0
[30 empty] | 97.3449 | 633.2107 |  |  |  | 0 | 0 | 0 | 1 |  | 2.6366 | 0.18789 |  |  | 0.18789 |  | 3 | 0
[19 empty] | 3.5109 | 0.8 |  |  |  |  | 100 | 1 | 22 |  |  | 2.6551 |  | 225 | 175 |  | 0 |  | 3.5109 | 3.5109 | 0.24 | 0.25113 | 0.25113 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 2.6332 | [5 empty] | 8.7224 |  | 3.3647 |  |  | 3.5109 | 2.6332 |  |  |  | 0 |  | 2.6332 | 2.6332 | 0.0883 | 0.18789 | 0.18789 |  | 1 |  |  | 50 | 0
| 82P3 -07 | No.8 Substation TR No8-1 #3S-1 ～#3L-30 | [9 empty] | Test machine | 3 | 0.8 | 0.8 | 4.6875 | 0.4 | 5.317 | 20.6615 |  | 600V CV-T |  |  | Cable -tray | 600V CV-T |  |  | Cable -tray | 198.6006 | 198.044 | 9.5852 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 | 1.08 | 16.5399 | 0.27043 | 0.2764 |  | 0.27043 | 198.1322 | 3 | 0
[13 empty] | 3.2 | 1 | 0.8 | 4 | 0.4 | 4.5371 | [11 empty] | 97.2711 | 586.6633 |  |  |  | 0 | 0 | 0 | 1 | 0.102 | 12.3979 | 0.20231 | 0.20679 |  | 0.20231 |  | 3 | 0
[19 empty] | 16.5292 | 0.8 | 22 | 1 | 24 |  | 22 | 1 | 6 |  |  | 2.7289 |  | 100 | 75 |  | 0 |  | 16.5292 | 16.5292 | 1.08 | 12.4635 | 12.5063 | 0.27043 | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 12.3969 |  | 42.8192 |  | 4.2401 |  | 10.7048 |  | 1.06 |  |  | 16.5292 | 12.3969 |  |  |  | 0 |  | 12.3969 | 12.3969 | 0.102 | 9.3404 | 9.3446 | 0.20231 | 1 |  |  | 50 | 0
|  | #3P-30 ～#3P-31 | [9 empty] | Test machine | 1.5 | 0.8 | 0.8 | 2.3438 | 0.4 | 2.6585 | 63.1197 | [5 empty] | 600V CV-3C |  |  | Cable -tray |  | 197.9408 | 3.136 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 50.5703 | 50.5703 |  |  | 50.5703 | 198.1322 | 3 | 0
[13 empty] | 0.4 | 1 | 0.8 | 0.5 | 0.4 | 0.56714 | [11 empty] | 97.2204 | 3.136 |  |  |  | 0 | 0 | 0 | 1 |  | 37.8741 | 37.8741 |  |  | 37.8741 |  | 3 | 0
[19 empty] | 50.4957 | 0.8 |  |  |  |  | 8 | 1 | 15 |  |  | 2.7796 |  |  |  |  | 0 |  | 50.4957 | 50.4957 | 3.01 | 50.5703 | 50.5703 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 37.8718 | [5 empty] | 74.5867 |  | 2.2603 |  | 198.1322 | 50.4957 | 37.8718 |  |  |  | 0 |  | 37.8718 | 37.8718 | 0.087 | 37.8741 | 37.8741 |  | 1 |  |  | 50 | 0
| 82P9 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.106 Control board(G3-13) | [9 empty] | Test machine | 62.4 | 1 | 0.8 | 78 | 0.4 | 88.4741 | 2.3012 | [5 empty] | 600V CE(NE)-T |  |  | Cable -tray | 198.6006 | 196.3176 | 85.3095 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.8646 | 0.2764 |  |  | 0.2764 | 198.6006 | 3 | 0
[12 empty] | G3-13 | [17 empty] | 96.4232 | 575.3292 |  |  |  | 0 | 0 | 0 | 1 |  | 1.3938 | 0.20679 |  |  | 0.20679 |  | 3 | 0
[19 empty] | 1.841 | 0.8 |  |  |  |  | 150 | 1 | 90 |  |  | 3.5768 |  | 225 | 225 |  | 0 |  | 1.841 | 1.841 | 0.159 | 0.2764 | 0.2764 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 1.3807 | [5 empty] | 23.6398 |  | 13.0787 |  |  | 1.841 | 1.3807 |  |  |  | 0 |  | 1.3807 | 1.3807 | 0.0839 | 0.20679 | 0.20679 |  | 1 |  |  | 50 | 0
| 82P4 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.102 Oil pressure unit(G2-5) | [9 empty] | Test machine | 104 | 1 | 0.8 | 130 | 0.4 | 147.4568 | 1.3807 | [5 empty] | 600V CE(NE)-T |  |  | Subtr.pipe Cabletray | 198.6006 | 197.0276 | 142.6968 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.1135 | 0.32451 |  |  | 0.32451 | 198.6006 | 3 | 0
[12 empty] | G2-5 | [17 empty] | 96.7719 | 490.0196 |  |  |  | 0 | 0 | 0 | 1 |  | 0.83496 | 0.24281 |  |  | 0.24281 |  | 3 | 0
[19 empty] | 1.1046 | 0.8 |  |  |  |  | 200 | 2 | 89 |  |  | 3.2281 |  | 400 | 400 |  | 0 |  | 1.1046 | 1.1046 | 0.121 | 0.32451 | 0.32451 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 0.82845 | [5 empty] | 8.8951 |  | 6.5129 |  |  | 1.1046 | 0.82845 |  |  |  | 0 |  | 0.82845 | 0.82845 | 0.0845 | 0.24281 | 0.24281 |  | 1 |  |  | 50 | 0
| 82P5 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.102 VCF Tester(G2-8) | [9 empty] | Test machine | 56 | 1 | 0.8 | 70 | 0.4 | 79.3998 | 2.5642 | [5 empty] | 600V CE(NE)-T |  |  | Subtr.pipe Cabletray | 198.6006 | 196.6622 | 76.6942 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 2.0737 | 0.45797 |  |  | 0.45797 | 198.6006 | 3 | 0
[12 empty] | G2-8 | [17 empty] | 96.5924 | 347.323 |  |  |  | 0 | 0 | 0 | 1 |  | 1.5509 | 0.34237 |  |  | 0.34237 |  | 3 | 0
[19 empty] | 2.0514 | 0.8 |  |  |  |  | 150 | 1 | 85 |  |  | 3.4076 |  | 225 | 200 |  | 0 |  | 2.0514 | 2.0514 | 0.159 | 0.45797 | 0.45797 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 1.5385 | [5 empty] | 22.3264 |  | 12.3521 |  |  | 2.0514 | 1.5385 |  |  |  | 0 |  | 1.5385 | 1.5385 | 0.0839 | 0.34237 | 0.34237 |  | 1 |  |  | 50 | 0
| 82P6 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.106 CAE#2Tester(ATF-36) | [9 empty] | Test machine | 62.4 | 1 | 0.8 | 78 | 0.4 | 88.4741 | 2.3012 | [5 empty] | 600V CE(NE)-T |  |  | Subtr.pipe Cabletray | 198.6006 | 196.2925 | 85.2986 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.8649 | 0.58778 |  |  | 0.58778 | 198.6006 | 3 | 0
[12 empty] | ATF-36 | [17 empty] | 96.4108 | 270.6287 |  |  |  | 0 | 0 | 0 | 1 |  | 1.394 | 0.43937 |  |  | 0.43937 |  | 3 | 0
[19 empty] | 1.841 | 0.8 |  |  |  |  | 150 | 1 | 91 |  |  | 3.5892 |  | 225 | 225 |  | 0 |  | 1.841 | 1.841 | 0.159 | 0.58778 | 0.58778 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 1.3807 | [5 empty] | 23.9024 |  | 13.224 |  |  | 1.841 | 1.3807 |  |  |  | 0 |  | 1.3807 | 1.3807 | 0.0839 | 0.43937 | 0.43937 |  | 1 |  |  | 50 | 0
| 82P7 | No.8 Substation TR No8-1 Switchboard(Existing) ～R/M No.106 CAE#2Tester(ATF-44) | [9 empty] | Test machine | 62.4 | 1 | 0.8 | 78 | 0.4 | 88.4741 | 2.3012 | [5 empty] | 600V CE(NE)-T |  |  | Subtr.pipe Cabletray | 198.6006 | 196.3426 | 85.3204 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.8644 | 0.85831 |  |  | 0.85831 | 198.6006 | 3 | 0
[12 empty] | ATF-44 | [17 empty] | 96.4355 | 185.3301 |  |  |  | 0 | 0 | 0 | 1 |  | 1.3937 | 0.6416 |  |  | 0.6416 |  | 3 | 0
[19 empty] | 1.841 | 0.8 |  |  |  |  | 150 | 1 | 89 |  |  | 3.5645 |  | 225 | 225 |  | 0 |  | 1.841 | 1.841 | 0.159 | 0.85831 | 0.85831 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 1.3807 | [5 empty] | 23.3771 |  | 12.9334 |  |  | 1.841 | 1.3807 |  |  |  | 0 |  | 1.3807 | 1.3807 | 0.0839 | 0.6416 | 0.6416 |  | 1 |  |  | 50 | 0
| 82P8 | No.8 Substation TR No8-1 Switchboard(Existing) ～#5P-1 | [9 empty] | Test machine | 4.7 | 0.8 | 0.8 | 7.3438 | 0.4 | 8.3299 | 1.9629 | [5 empty] | 600V CE(NE)-T |  |  | Subtr.pipe Cabletray | 198.6006 | 196.3108 | 100.0097 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 1.5906 | 1.5906 |  |  | 1.5906 | 198.6006 | 3 | 0
[13 empty] | 67.28 | 1 | 0.8 | 84.1 | 0.4 | 95.3932 | [11 empty] | 96.4198 |  |  |  |  | 0 | 0 | 0 | 1 |  | 1.1889 | 1.1889 |  |  | 1.1889 |  | 3 | 0
[19 empty] | 1.5703 | 0.8 |  |  |  |  | 150 | 1 | 77 |  |  | 3.5802 |  | 225 | 225 |  | 0 |  | 1.5703 | 1.5703 | 0.159 | 1.5906 | 1.5906 |  | 0 |  | 198.6006 | 203.6 | 0
|  |  | 75 | [15 empty] | 1.1778 | [5 empty] | 20.2251 |  | 11.1896 |  |  | 1.5703 | 1.1778 |  |  |  | 0 |  | 1.1778 | 1.1778 | 0.0839 | 1.1889 | 1.1889 |  | 1 |  |  | 50 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 2 |  |  | 0 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 3 |  |  | 0 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 4 |  |  | 0 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 5 |  |  | 0 | 0
|  | TGCRDL Relocation Project | [13 empty] | ESE-VD4 Exchange circuit analysis calculation | [5 empty] | Co.,Ltd. Yoshimura Airchitecture Design Office | [6 empty] | K,Yoshimura |  | K,Sakai |  |  | Terminal voltage -08 (Standard)
Note on B12: Drop down LIST An addition, change, and deletion can do this registration cell.
Note on B46: Drop down LIST An addition, change, and deletion can do this registration cell.
Note on C8: Printing range
Note on F13: Please input the temperature of conductor for calculation. (Each line) -100[℃] ～ +300[℃] Attention: It calculates by 0[℃] if it does not input. Ａｂｏｕｔ ｔｈｅ ｔｅｍｐｅｒａｔｕｒｅ ｏｆ ｃｏｎｄｕｃｔｏｒ The degree 20[℃] is standard temperature. Generally, this temperature is 50-60 [℃] except for a cold district. Please decide on reference by carrying out the maximum per- mission temperature of a conductor.
Note on L3: It can use for the power transmission voltage at the time of regular of an independent trunk and a branch trunk, received voltage, load current, the check of power factor, the determination of series capacitor capacity, etc. Comment ■ is the object for cells which needs an input． ■ is an explanatory note etc. Input cell ■ should input a required matter. Calculation cell ■ is an automatic calculation cell, an input is impossible.
Note on L11: ↓Please choose out of a drop down list. When Liszt does not have [except oil cooled type and (F)-molded type], please perform after inputting data into the "transformer USER" of DATA Table.
Note on L13: Following transformer data is registered into DATA Table. （50/60Hz） ３φ３Ｗ－２０ ～ １０００［ＫＶＡ］ １φ３Ｗ－１０ ～ ５００［ＫＶＡ］ An exact value will be calculated if the change correction of the %R and %X of an adoption transformer is made by DATA Table. Calculation of transformer rated current is depended below. In the case of ３φ：TRcap／(√3 x Es) In the case of １φ：TRcap／ Es TRcap：Capacity of TR. Es：Secondary voltage of TR.
Note on M11: When a transformer is parallel operation, please input the number of a parallel transformer.
Note on N6: 翻訳ができません６％） 10, 15, 20, 25, 30, 40, 50, 75,100[KVar] 400，415，440，460V-50Hz，60Hz（直列リアクトルなし） 10, 15, 20, 25, 30, 50, 75,100,150[KVar] 400，415，440，460V-50Hz，60Hz（直列リアクトル6％） 10, 15, 20, 25, 30, 50, 75,100,150,200 250,300[KVar]
Note on N10: Ｓｅｒｉｅｓ ｐｏｗｅｒ ｃａｐａｃｉｔｏｒ When average power factor of total load is bad (delay), SC improves power factor, and it installs the electric power transfor- mer by the side of power distribution in order to operate efficiently.
Note on O10: When you perform accumulation calculation, be careful of the following point. Trunk branch etc., when you accumulate the voltage drop value of each section, please use four lines each of a "cell" continuously. When you move to independent trunk calculation or next another calculation, four or more lines should vacate and please be sure to input a cell.
Note on O11: Please choose out of a drop down list.
Note on Q11: In the case of induction motor load, please input in the range of ０＜～１．０００ In the case of other loads, please input ”１”
Note on R11: Please input the value of the range of ０＜～１．０００
Note on S11: Iｎｐｕｔ ＫＶＡ Input ＫＶＡ＝Output ＫＷ／（ｃｏｓφｘη） cosφ ：Power factor of Load η ：Efficiency of Load
Note on W10: Load side Series Power Capacitor SC improves delay power factor of induc- tive load, reduces voltage drop of a trunk, and it installs it in order to prevent the fall of primary voltage.
Note on X11: Please choose out of a drop down list. In inputting the size which is not in a data table, please register R and X (50Hz) of the cable into a data table.
Note on Z11: Please input the fruit length meter of a cable.
Note on AA10: Please choose out of a drop down list.
Note on AB11: Please choose out of a drop down list. In inputting the size which is not in a data table, please register R and X (50Hz) of the cable into a data table.
Note on AD11: Please input the fruit length meter of a cable.
Note on AE10: Please choose out of a drop down list.
Note on AF10: Secondary transformer side voltage ［Ｖ］
Note on AF13: Voltage of the circuit diagram EB section ［Ｖ］
Note on AG11: Percent to power supply voltage [％]
Note on AG12: Percent of line voltage drop to power supply voltage [％]
Note on AJ11: ↓Please choose out of a drop down list. The important matter about selection of the frame / trip value of MCCB １） The check of interception capacity ２） The characteristic and the temperature conditions of MCCB ３） Grasp of the real load current which took into consideration the demand factor, load factor, divercity factor,voltage regulation rate of transformer, unbalance factor, etc. at the time of regular operation of a motor, at the time of starting of a motor. Frame value [A] of MCCB（Ｍｏｌｄｅｄ ｃａｓｅ ｃｉｒｃｕｉｔ ｂｒｅａｋｅｒ） ３０， ５０， ６０， １００， ２２５， ２５０， ４００， ６００， ８００，１０００， １２００，１６００，２０００，２５００，３０００， ３２００，４０００ Frame value [A] of ＡＣＢ（Ａｉｒ ｃｉｒｃｕｉｔ ｂｒｅａｋｅｒ） ６３０，１０００，１２５０，１６００，２０００， ２５００，３２００，４０００，５０００，６３００
Note on AJ12: Please choose out of a drop down list.
Note on AJ13: Please choose out of a drop down list.
Approved
Checked
Input cell
Exchange circuit analisys calculation -VD４
２００２ Ａｕｇ． Ｖｅｒ ２．0 by ＥＳＥ SERVICE
Automatic display
A "comment" will be displayed if cursor is brought close to the cell of upper right red.

## TR84･85
⇒
0.11838
High volt. Capacitor
Low volt. Capacitor
2002/08/01 Ver1.4
| Trunk number | Application section | Electric system | [5 empty] | Distribution side apparatus |  |  | Load side apparatus | [8 empty] | Selection-1 (Branch trunk) |  |  |  | Selection-2 (Trunk) |  |  |  | Transmission | Reception |  | Distribution |  | Note
|  |  | Sec. voltage ES[V] | [5 empty] | Power transformer |  | SCS Capacity | Load equipment capacity | [7 empty] | SCL Capacity | Cable name |  |  | Construct | Cable name |  |  | Construct | Voltage ER [V] | Voltage ＥＬ[V] | Current IL [A] | side |  |  | 1 phi-R | User-R | SCS | nphinW-1 | R-C1n | R-n2 | R-n4 |  |  | R-01 | E-Cn | Phi-G 20 | Load classification
|  |  | φ |  | W |  | V |  | Form | Number |  | Load classification | Output | Effici- ency | Power factor | Input | Demand factor | Load current | Ｚ Ｌ [Ω] |  | Cross | No. | Cable | Permission current[A] | Cross | No. | Cable | Permission current[A] | All load [A] | ＥＬ／Ｅ[％] | Current IC [A] | Breaker |  |  | 1 phi-X | User-X | SCLoad | nphinW-2 | X-C1n | X-n2 | X-n4 |  |  | X-01 |  | w-I20
Drop down LIST |  |  | Frequency [Hz] | [6 empty] | ％ Z | [Kvar] | [7 empty] | Ｒ Ｌ [Ω] | [Kvar] | section |  | span |  | section |  | span |  | TR current [A] | (Ｅ-ＥＬ)／Ｅ[％] | (Total) | Name |  |  | 3 phi-R | R-TR | R-n1 | R-n1' | R-C2n | R-n3 | R-n4' | R-n4' |  | R-02 | ES | E-K20
Load Classification |  |  | Calculation temp. | [5 empty] | Capacity/Rated current |  |  |  | [KW] | η | cosφ | [KVA] | Df | [A] | Ｘ Ｌ [Ω] | Avrg. PF | Ｚ Ｃ１ (Trunk) |  |  |  | Ｚ Ｃ２ (Branch trunk) |  |  |  | Branch part [V] | Zｎ１（Ｌｎ＋ＣＬ１） |  | -AF | -AT |  | 3 phi-X | X-TR | X-n1 | X-n1' | X-C2n | X-n3 | X-n4' | X-n4' |  | X-02 |  | Hz-G22
|  | No.8 Substation TR No.8-4 SC: 0KVar | [33 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
Prod. power | [35 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
Experimental eq. | [37 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
AC M/C | [37 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
Supply fan | 84P1 | No.8 Substation TR No8-4 Switchboard(New) ～#3P-R1 | 3 | φ | 3 | W | 210 | V | oil cooled type | 1 |  | AC power | 50.66 | 0.8 | 0.8 | 79.1562 | 0.6 | 130.5739 | 1.4089 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.3283 | 201.2498 | 142.8386 |  |  | Load factor of transformer | 0 | 0 | 0 | 1.7321 |  | 1.1445 | 0.11838 |  |  | 0.11838 | 204.3283 | 3 | 0
Exhaust fan | [9 empty] | 5.0914 |  |  | 8.96 | 1 | 0.8 | 11.2 | 0.6 | 18.4752 | [10 empty] | 1381.4011 | 95.8332 | 1381.4011 |  |  | 66.99 ％ | 0 | 0 | 0 | 1 |  | 0.85809 | 0.088677 |  |  | 0.088677 |  | 3 | 0
|  |  | 50 | [5 empty] | 750 | [9 empty] | 1.1271 | 0.8 |  |  |  |  | 200 | 1 | 87 |  | 1381.4011 | 4.1668 |  |  |  |  | 1.31 | 0.0013342 | 1.1271 | 1.1271 | 0.121 | 0.11838 | 0.11838 |  | 0 | 0.11972 | 204.3283 | 210 | 0
sanitation |  |  | 75 | [5 empty] | 2061.9652 | [9 empty] | 0.84536 | [5 empty] | 17.3903 |  | 12.7332 |  |  | 1.1271 | 0.84536 |  |  |  | 4.92 | 0.0050108 | 0.84536 | 0.84536 | 0.0845 | 0.088677 | 0.088677 |  | 1 | 0.093688 |  | 50 | 0
Septic tank | 84P2 | No.8 Substation TR No8-4 Switchboard(New) ～#3P-R1 | [9 empty] | AC power | 48.94 | 0.8 | 0.8 | 76.4688 | 0.6 | 126.1407 | 1.4293 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.3283 | 201.293 | 140.8335 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 1.1608 | 0.13204 |  |  | 0.13204 | 204.3283 | 3 | 0
[13 empty] | 10.08 | 1 | 0.8 | 12.6 | 0.6 | 20.7846 | [11 empty] | 95.8538 | 1238.5624 |  |  |  | 0 | 0 | 0 | 1 |  | 0.87031 | 0.098897 |  |  | 0.098897 |  | 3 | 0
[19 empty] | 1.1434 | 0.8 |  |  |  |  | 200 | 1 | 87 |  |  | 4.1462 |  |  |  |  | 0 |  | 1.1434 | 1.1434 | 0.121 | 0.13204 | 0.13204 |  | 0 |  | 204.3283 | 210 | 0
Existing load |  |  | 75 | [15 empty] | 0.85758 | [5 empty] | 17.3903 |  | 12.7332 |  |  | 1.1434 | 0.85758 |  |  |  | 0 |  | 0.85758 | 0.85758 | 0.0845 | 0.098897 | 0.098897 |  | 1 |  |  | 50 | 0
| 84P3 | No.8 Substation TR No8-4 Switchboard(New) ～#3P-R2 | [9 empty] | AC power | 68.33 | 0.8 | 0.8 | 106.7656 | 0.6 | 176.1176 | 1.0977 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.3283 | 200.9746 | 183.088 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 0.89193 | 0.14899 |  |  | 0.14899 | 204.3283 | 3 | 0
[13 empty] | 7.368 | 1 | 0.8 | 9.21 | 0.6 | 15.1926 | [11 empty] | 95.7022 | 1097.7289 |  |  |  | 0 | 0 | 0 | 1 |  | 0.67078 | 0.11158 |  |  | 0.11158 |  | 3 | 0
Lighting Load | [18 empty] | 0.87816 | 0.8 |  |  |  |  | 250 | 1 | 85 |  |  | 4.2978 |  |  |  |  | 0 |  | 0.87816 | 0.87816 | 0.0981 | 0.14899 | 0.14899 |  | 0 |  | 204.3283 | 210 | 0
Wall socket |  |  | 75 | [15 empty] | 0.65862 | [5 empty] | 13.775 |  | 12.1607 |  |  | 0.87816 | 0.65862 |  |  |  | 0 |  | 0.65862 | 0.65862 | 0.0826 | 0.11158 | 0.11158 |  | 1 |  |  | 50 | 0
| 84P4 | No.8 Substation TR No8-4 Switchboard(New) ～#4P-1 | [9 empty] | AC power | 28.64 | 0.8 | 0.8 | 44.75 | 0.6 | 73.8184 | 2.7083 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.3283 | 202.5683 | 74.7961 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 2.1915 | 0.17887 |  |  | 0.17887 | 204.3283 | 3 | 0
[13 empty] | 1.68 | 1 | 0.8 | 2.1 | 0.6 | 3.4641 | [11 empty] | 96.4611 | 914.6413 |  |  |  | 0 | 0 | 0 | 1 |  | 1.6309 | 0.13384 |  |  | 0.13384 |  | 3 | 0
[12 empty] | Exhaust fan | 1.2 | 0.8 | 0.8 | 1.875 | 0.05 | 0.25775 | 2.1666 | 0.8 |  |  |  |  | 60 | 1 | 38 |  |  | 3.5389 |  |  |  |  | 0 |  | 2.1666 | 2.1666 | 0.397 | 0.17887 | 0.17887 |  | 0 |  | 204.3283 | 210 | 0
|  |  | 75 | [15 empty] | 1.625 | [5 empty] | 24.9217 |  | 5.9565 |  |  | 2.1666 | 1.625 |  |  |  | 0 |  | 1.625 | 1.625 | 0.0905 | 0.13384 | 0.13384 |  | 1 |  |  | 50 | 0
| 84P5 | No.8 Substation TR No8-4 Switchboard(New) ～R-1 | [9 empty] | Chiller | 64 | 0.8 | 0.8 | 100 | 0.6 | 164.9572 | 1.2667 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.3283 | 201.9579 | 159.4332 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 1.0265 | 0.19476 |  |  | 0.19476 | 204.3283 | 3 | 0
[12 empty] | (Air cooling) | 0.4 | 1 | 0.8 | 0.5 | 0.6 | 0.82479 | [11 empty] | 96.1704 | 839.8455 |  |  |  | 0 | 0 | 0 | 1 |  | 0.7673 | 0.1458 |  |  | 0.1458 |  | 3 | 0
[19 empty] | 1.0134 | 0.8 |  |  |  |  | 150 | 1 | 50 |  |  | 3.8296 |  |  |  |  | 0 |  | 1.0134 | 1.0134 | 0.159 | 0.19476 | 0.19476 |  | 0 |  | 204.3283 | 210 | 0
|  |  | 75 | [15 empty] | 0.76003 | [5 empty] | 13.1332 |  | 7.266 |  |  | 1.0134 | 0.76003 |  |  |  | 0 |  | 0.76003 | 0.76003 | 0.0839 | 0.1458 | 0.1458 |  | 1 |  |  | 50 | 0
| 84P6 | No.8 Substation TR No8-4 Switchboard(New) ～R-5 | [9 empty] | Chiller | 64 | 0.8 | 0.8 | 100 | 0.6 | 164.9572 | 1.2667 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.3283 | 201.7238 | 159.2485 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 1.0278 | 0.24037 |  |  | 0.24037 | 204.3283 | 3 | 0
[12 empty] | (Air cooling) | 0.4 | 1 | 0.8 | 0.5 | 0.6 | 0.82479 | [11 empty] | 96.059 | 680.4123 |  |  |  | 0 | 0 | 0 | 1 |  | 0.76803 | 0.18001 |  |  | 0.18001 |  | 3 | 0
[19 empty] | 1.0134 | 0.8 |  |  |  |  | 150 | 1 | 55 |  |  | 3.941 |  |  |  |  | 0 |  | 1.0134 | 1.0134 | 0.159 | 0.24037 | 0.24037 |  | 0 |  | 204.3283 | 210 | 0
|  |  | 75 | [15 empty] | 0.76003 | [5 empty] | 14.4465 |  | 7.9925 |  |  | 1.0134 | 0.76003 |  |  |  | 0 |  | 0.76003 | 0.76003 | 0.0839 | 0.18001 | 0.18001 |  | 1 |  |  | 50 | 0
Drop down LIST | 84P7 | No.8 Substation TR No8-4 Switchboard(New) ～#4P-2 | [9 empty] | AC power | 81.8 | 0.8 | 0.8 | 127.8125 | 0.6 | 210.8359 | 0.99215 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.3283 | 201.8089 | 203.4048 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 0.80372 | 0.31374 |  |  | 0.31374 | 204.3283 | 3 | #REF!
construction of cable | [12 empty] | 0.4 | 1 | 0.8 | 0.5 | 0.6 | 0.82479 | [11 empty] | 96.0995 | 521.1639 |  |  |  | 0 | 0 | 0 | 1 |  | 0.60261 | 0.23511 |  |  | 0.23511 |  | 3 | 0
[19 empty] | 0.79372 | 0.8 |  |  |  |  | 200 | 1 | 50 |  |  | 3.9005 |  |  |  |  | 0 |  | 0.79372 | 0.79372 | 0.121 | 0.31374 | 0.31374 |  | 0 |  | 204.3283 | 210 | 0
Cabletray |  |  | 75 | [15 empty] | 0.59529 | [5 empty] | 9.9945 |  | 7.3179 |  |  | 0.79372 | 0.59529 |  |  |  | 0 |  | 0.59529 | 0.59529 | 0.0845 | 0.23511 | 0.23511 |  | 1 |  |  | 50 | 0
Subter- ranean | 84P8 | No.8 Substation TR No8-4 Switchboard(New) ～#5P-2 | [9 empty] | AC power | 28.51 | 0.8 | 0.8 | 44.5469 | 0.6 | 73.4833 | 2.5437 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.3283 | 201.1919 | 79.0932 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 2.077 | 0.51464 |  |  | 0.51464 | 204.3283 | 3 | 0
Under drain | [12 empty] | 4.4 | 1 | 0.8 | 5.5 | 0.6 | 9.0726 | [11 empty] | 95.8056 | 317.7591 |  |  |  | 0 | 0 | 0 | 1 |  | 1.5363 | 0.38553 |  |  | 0.38553 |  | 3 | 0
Openpit | [18 empty] | 2.035 | 0.8 |  |  |  |  | 60 | 1 | 64 |  |  | 4.1944 |  |  |  |  | 0 |  | 2.035 | 2.035 | 0.397 | 0.51464 | 0.51464 |  | 0 |  | 204.3283 | 210 | 0
Exposure piping |  |  | 75 | [15 empty] | 1.5262 | [5 empty] | 41.9734 |  | 10.032 |  |  | 2.035 | 1.5262 |  |  |  | 0 |  | 1.5262 | 1.5262 | 0.0905 | 0.38553 | 0.38553 |  | 1 |  |  | 50 | 0
Conceal. piping | 84P9 | No.8 Substation TR No8-4 Switchboard(New) ～Control board (Existing) | [9 empty] | AC power | 96.95 | 0.8 | 0.8 | 151.4844 | 0.6 | 249.8844 | 0.84039 | [5 empty] | 600V CE(NE)-T |  |  |  | 204.3283 | 200.5737 | 238.6678 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 0.68414 | 0.68414 |  |  | 0.68414 | 204.3283 | 3 | 0
[30 empty] | 95.5113 |  |  |  |  | 0 | 0 | 0 | 1 |  | 0.51468 | 0.51468 |  |  | 0.51468 |  | 3 | 0
[19 empty] | 0.67231 | 0.8 |  |  |  |  | 250 | 1 | 73 |  |  | 4.4887 |  |  |  |  | 0 |  | 0.67231 | 0.67231 | 0.0981 | 0.68414 | 0.68414 |  | 0 |  | 204.3283 | 210 | 0
|  |  | 75 | [15 empty] | 0.50423 | [5 empty] | 11.8303 |  | 10.4439 |  |  | 0.67231 | 0.50423 |  |  |  | 0 |  | 0.50423 | 0.50423 | 0.0826 | 0.51468 | 0.51468 |  | 1 |  |  | 50 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 2 |  |  | 0 | 0
|  | No.8 Substation TR No.8-5 SC: 0KVar | [33 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 3 |  |  | 0 | 0
| 85P1 | No.8 Substation TR No8-5 Switchboard(New) ～CHDY Analysis meter | 3 | φ | 3 | W | 210 | V | oil cooled type | 1 |  | Test machine | 216 | 1 | 0.8 | 270 | 0.7 | 519.6152 | 0.40415 | [5 empty] | 600V CE(NE)-T |  |  |  | 205.9942 | 200.5843 | 496.3174 | MCCB-3P |  | Load factor of transformer | 0 | 0 | 0 | 1.7321 |  | 0.33211 | 0.30361 |  |  | 0.30361 | 205.9942 | 3 | 0
[10 empty] | 3.1941 | [18 empty] | 543.0477 | 95.5163 | 543.0477 |  |  | 65.84 ％ | 0 | 0 | 0 | 1 |  | 0.24893 | 0.2274 |  |  | 0.2274 |  | 3 | 0
|  |  | 50 | [5 empty] | 300 | [9 empty] | 0.32332 | 0.8 |  |  |  |  | 200 | 2 | 88 |  | 543.0477 | 4.4837 |  | 800 | 800 |  | 1.5 | 0.0038192 | 0.32332 | 0.32332 | 0.121 | 0.30361 | 0.30361 |  | 0 | 0.30743 | 205.9942 | 210 | 0
|  |  | 75 | [5 empty] | 824.7861 | [9 empty] | 0.24249 | [5 empty] | 8.7951 |  | 6.4398 |  |  | 0.32332 | 0.24249 |  |  |  | 2.82 | 0.00718 | 0.24249 | 0.24249 | 0.0845 | 0.2274 | 0.2274 |  | 3 | 0.23458 |  | 50 | 0
| 85P2 | No.8 Substation TR No8-5 Switchboard(New) ～CVT equipment | [9 empty] | Test machine | 20 | 1 | 0.8 | 25 | 0.7 | 48.1125 | 4.3648 | [5 empty] | 600V CE(NE)-T |  |  |  | 205.9942 | 203.9684 | 46.7306 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 3.5377 | 3.5377 |  |  | 3.5377 | 205.9942 | 3 | 0
[30 empty] | 97.1278 |  |  |  |  | 0 | 0 | 0 | 1 |  | 2.6298 | 2.6298 |  |  | 2.6298 |  | 3 | 0
[19 empty] | 3.4918 | 0.8 |  |  |  |  | 60 | 1 | 70 |  |  | 2.8722 |  | 100 | 75 |  | 0 |  | 3.4918 | 3.4918 | 0.397 | 3.5377 | 3.5377 |  | 0 |  | 205.9942 | 210 | 0
|  |  | 75 | [15 empty] | 2.6189 | [5 empty] | 45.9084 |  | 10.9725 |  |  | 3.4918 | 2.6189 |  |  |  | 0 |  | 2.6189 | 2.6189 | 0.0905 | 2.6298 | 2.6298 |  | 3 |  |  | 50 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 4 |  |  | 0 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 5 |  |  | 0 | 0
[38 empty] | 1e+30 | [7 empty] | 0 | 0
|  | TGCRDL Relocation Project | [13 empty] | ESE-VD4 Exchange circuit analysis calculation | [5 empty] | Co.,Ltd. Yoshimura Airchitecture Design Office | [6 empty] | K,Yoshimura |  | K,Sakai |  |  | Terminal voltage -09 (Standard)
Note on B12: Drop down LIST An addition, change, and deletion can do this registration cell.
Note on B46: Drop down LIST An addition, change, and deletion can do this registration cell.
Note on C8: Printing range
Note on F13: Please input the temperature of conductor for calculation. (Each line) -100[℃] ～ +300[℃] Attention: It calculates by 0[℃] if it does not input. Ａｂｏｕｔ ｔｈｅ ｔｅｍｐｅｒａｔｕｒｅ ｏｆ ｃｏｎｄｕｃｔｏｒ The degree 20[℃] is standard temperature. Generally, this temperature is 50-60 [℃] except for a cold district. Please decide on reference by carrying out the maximum per- mission temperature of a conductor.
Note on L3: It can use for the power transmission voltage at the time of regular of an independent trunk and a branch trunk, received voltage, load current, the check of power factor, the determination of series capacitor capacity, etc. Comment ■ is the object for cells which needs an input． ■ is an explanatory note etc. Input cell ■ should input a required matter. Calculation cell ■ is an automatic calculation cell, an input is impossible.
Note on L11: ↓Please choose out of a drop down list. When Liszt does not have [except oil cooled type and (F)-molded type], please perform after inputting data into the "transformer USER" of DATA Table.
Note on L13: Following transformer data is registered into DATA Table. （50/60Hz） ３φ３Ｗ－２０ ～ １０００［ＫＶＡ］ １φ３Ｗ－１０ ～ ５００［ＫＶＡ］ An exact value will be calculated if the change correction of the %R and %X of an adoption transformer is made by DATA Table. Calculation of transformer rated current is depended below. In the case of ３φ：TRcap／(√3 x Es) In the case of １φ：TRcap／ Es TRcap：Capacity of TR. Es：Secondary voltage of TR.
Note on M11: When a transformer is parallel operation, please input the number of a parallel transformer.
Note on N6: High-voltage Capacitor［Nichicon Corp.1991.5］ 3300V，6600V-50Hz，60Hz（no Series reactor） 50, 75,100,150,200,250,300 [KVar] 3300V，6600V-50Hz，60Hz（Series reactor 6％） 50, 75,100,150,200,250,300,400,500,600, 700,750,800,900,1000[KVar] 3300V，6600V-50Hz，60Hz（Series reactor 13％） 50, 75,100,150,200,250,300,400,500[KVar]
Note on N7: Low-voltage Capacitor［Nichicon Corp.1991.5］ 200V，220V-50Hz，60Hz（no Series reactor） 10, 15, 20, 25, 30, 50[KVar] 200V，220V-50Hz，60Hz（Series reactor ６％） 10, 15, 20, 25, 30, 40, 50, 75,100[KVar] 400，415，440，460V-50Hz，60Hz（no Series reactor） 10, 15, 20, 25, 30, 50, 75,100,150[KVar] 400，415，440，460V-50Hz，60Hz（Series reactor 6％） 10, 15, 20, 25, 30, 50, 75,100,150,200 250,300[KVar]
Note on N10: Ｓｅｒｉｅｓ ｐｏｗｅｒ ｃａｐａｃｉｔｏｒ When average power factor of total load is bad (delay), SC improves power factor, and it installs the electric power transfor- mer by the side of power distribution in order to operate efficiently.
Note on O10: When you perform accumulation calculation, be careful of the following point. Trunk branch etc., when you accumulate the voltage drop value of each section, please use four lines each of a "cell" continuously. When you move to independent trunk calculation or next another calculation, four or more lines should vacate and please be sure to input a cell.
Note on O11: Please choose out of a drop down list.
Note on Q11: In the case of induction motor load, please input in the range of ０＜～１．０００ In the case of other loads, please input ”１”
Note on R11: Please input the value of the range of ０＜～１．０００
Note on S11: Iｎｐｕｔ ＫＶＡ Input ＫＶＡ＝Output ＫＷ／（ｃｏｓφｘη） cosφ ：Power factor of Load η ：Efficiency of Load
Note on W10: Load side Series Power Capacitor SC improves delay power factor of induc- tive load, reduces voltage drop of a trunk, and it installs it in order to prevent the fall of primary voltage.
Note on X11: Please choose out of a drop down list. In inputting the size which is not in a data table, please register R and X (50Hz) of the cable into a data table.
Note on Z11: Please input the fruit length meter of a cable.
Note on AA10: Please choose out of a drop down list.
Note on AB11: Please choose out of a drop down list. In inputting the size which is not in a data table, please register R and X (50Hz) of the cable into a data table.
Note on AD11: Please input the fruit length meter of a cable.
Note on AE10: Please choose out of a drop down list.
Note on AF10: Secondary transformer side voltage ［Ｖ］
Note on AF13: Voltage of the circuit diagram EB section ［Ｖ］
Note on AG11: Percent to power supply voltage [％]
Note on AG12: Percent of line voltage drop to power supply voltage [％]
Note on AJ11: ↓Please choose out of a drop down list. The important matter about selection of the frame / trip value of MCCB １） The check of interception capacity ２） The characteristic and the temperature conditions of MCCB ３） Grasp of the real load current which took into consideration the demand factor, load factor, divercity factor,voltage regulation rate of transformer, unbalance factor, etc. at the time of regular operation of a motor, at the time of starting of a motor. Frame value [A] of MCCB（Ｍｏｌｄｅｄ ｃａｓｅ ｃｉｒｃｕｉｔ ｂｒｅａｋｅｒ） ３０， ５０， ６０， １００， ２２５， ２５０， ４００， ６００， ８００，１０００， １２００，１６００，２０００，２５００，３０００， ３２００，４０００ Frame value [A] of ＡＣＢ（Ａｉｒ ｃｉｒｃｕｉｔ ｂｒｅａｋｅｒ） ６３０，１０００，１２５０，１６００，２０００， ２５００，３２００，４０００，５０００，６３００
Note on AJ12: Please choose out of a drop down list.
Note on AJ13: Please choose out of a drop down list.
Input cell
Exchange circuit analisys calculation -VD４
２００２ Ａｕｇ． Ｖｅｒ ２．0 by ＥＳＥ SERVICE
Automatic display
A "comment" will be displayed if cursor is brought close to the cell of upper right red.
Approved
Checked

## TR84･85SC
⇒
0.11838
High volt. Capacitor
Low volt. Capacitor
2002/08/01 Ver1.4
| Trunk number | Application section | Electric system | [5 empty] | Distribution side apparatus |  |  | Load side apparatus | [8 empty] | Selection-1 (Branch trunk) |  |  |  | Selection-2 (Trunk) |  |  |  | Transmission | Reception |  | Distribution |  | Note
|  |  | Sec. voltage ES[V] | [5 empty] | Power transformer |  | SCS Capacity | Load equipment capacity | [7 empty] | SCL Capacity | Cable name |  |  | Construct | Cable name |  |  | Construct | Voltage ER [V] | Voltage ＥＬ[V] | Current IL [A] | side |  |  | 1 phi-R | User-R | SCS | nphinW-1 | R-C1n | R-n2 | R-n4 |  |  | R-01 | E-Cn | Phi-G 20 | Load classification
|  |  | φ |  | W |  | V |  | Form | Number |  | Load classification | Output | Effici- ency | Power factor | Input | Demand factor | Load current | Ｚ Ｌ [Ω] |  | Cross | No. | Cable | Permission current[A] | Cross | No. | Cable | Permission current[A] | All load [A] | ＥＬ／Ｅ[％] | Current IC [A] | Breaker |  |  | 1 phi-X | User-X | SCLoad | nphinW-2 | X-C1n | X-n2 | X-n4 |  |  | X-01 |  | w-I20
Drop down LIST |  |  | Frequency [Hz] | [6 empty] | ％ Z | [Kvar] | [7 empty] | Ｒ Ｌ [Ω] | [Kvar] | section |  | span |  | section |  | span |  | TR current [A] | (Ｅ-ＥＬ)／Ｅ[％] | (Total) | Name |  |  | 3 phi-R | R-TR | R-n1 | R-n1' | R-C2n | R-n3 | R-n4' | R-n4' |  | R-02 | ES | E-K20
Load Classification |  |  | Calculation temp. | [5 empty] | Capacity/Rated current |  |  |  | [KW] | η | cosφ | [KVA] | Df | [A] | Ｘ Ｌ [Ω] | Avrg. PF | Ｚ Ｃ１ (Trunk) |  |  |  | Ｚ Ｃ２ (Branch trunk) |  |  |  | Branch part [V] | Zｎ１（Ｌｎ＋ＣＬ１） |  | -AF | -AT |  | 3 phi-X | X-TR | X-n1 | X-n1' | X-C2n | X-n3 | X-n4' | X-n4' |  | X-02 |  | Hz-G22
|  | No.8 Substation TR No.8-4 SC:200KVar | [33 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
Prod. power | [35 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
Experimental eq. | [37 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
AC M/C | [37 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
Supply fan | 84P1 | No.8 Substation TR No8-4 Switchboard(New) ～#3P-R1 | 3 | φ | 3 | W | 210 | V | oil cooled type | 1 | 200 | AC power | 50.66 | 0.8 | 0.8 | 79.1562 | 0.6 | 130.5739 | 1.4089 | [5 empty] | 600V CE(NE)-T |  |  |  | 206.9533 | 203.8353 | 144.6737 |  |  | Load factor of transformer | 0 | 0 | 2.6184 | 1.7321 |  | 1.1445 | 0.11838 |  |  | 0.17267 | 206.9533 | 3 | 0
Exhaust fan | [9 empty] | 5.0914 |  |  | 8.96 | 1 | 0.8 | 11.2 | 0.6 | 18.4752 | [10 empty] | 1399.1482 | 97.0644 | 1399.1482 |  |  | 56.18 ％ | 0 | 0 | 0 | 1 |  | 0.85809 | 0.088677 |  |  | 0.045785 |  | 3 | 0
|  |  | 50 | [5 empty] | 750 | [9 empty] | 1.1271 | 0.8 |  |  |  |  | 200 | 1 | 87 |  | 1158.5226 | 2.9356 |  |  |  |  | 1.31 | 0.0013342 | 1.1271 | 1.1271 | 0.121 | 0.11838 | 0.11838 |  | 0 | 0.174 | 206.9533 | 210 | 0
sanitation |  |  | 75 | [5 empty] | 2061.9652 | [9 empty] | 0.84536 | [5 empty] | 17.3903 |  | 12.7332 |  |  | 1.1271 | 0.84536 |  |  |  | 4.92 | 0.0050108 | 0.84536 | 0.84536 | 0.0845 | 0.088677 | 0.088677 |  | 1 | 0.050796 |  | 50 | 0
Septic tank | 84P2 | No.8 Substation TR No8-4 Switchboard(New) ～#3P-R1 | [9 empty] | AC power | 48.94 | 0.8 | 0.8 | 76.4688 | 0.6 | 126.1407 | 1.4293 | [5 empty] | 600V CE(NE)-T |  |  |  | 206.9533 | 203.8791 | 142.6429 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 1.1608 | 0.13204 |  |  | 0.13204 | 206.9533 | 3 | 0
[13 empty] | 10.08 | 1 | 0.8 | 12.6 | 0.6 | 20.7846 | [11 empty] | 97.0853 | 1254.4745 |  |  |  | 0 | 0 | 0 | 1 |  | 0.87031 | 0.098897 |  |  | 0.098897 |  | 3 | 0
[19 empty] | 1.1434 | 0.8 |  |  |  |  | 200 | 1 | 87 |  |  | 2.9147 |  |  |  |  | 0 |  | 1.1434 | 1.1434 | 0.121 | 0.13204 | 0.13204 |  | 0 |  | 206.9533 | 210 | 0
Existing load |  |  | 75 | [15 empty] | 0.85758 | [5 empty] | 17.3903 |  | 12.7332 |  |  | 1.1434 | 0.85758 |  |  |  | 0 |  | 0.85758 | 0.85758 | 0.0845 | 0.098897 | 0.098897 |  | 1 |  |  | 50 | 0
| 84P3 | No.8 Substation TR No8-4 Switchboard(New) ～#3P-R2 | [9 empty] | AC power | 68.33 | 0.8 | 0.8 | 106.7656 | 0.6 | 176.1176 | 1.0977 | [5 empty] | 600V CE(NE)-T |  |  |  | 206.9533 | 203.5566 | 185.4402 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 0.89193 | 0.14899 |  |  | 0.14899 | 206.9533 | 3 | 0
[13 empty] | 7.368 | 1 | 0.8 | 9.21 | 0.6 | 15.1926 | [11 empty] | 96.9317 | 1111.8316 |  |  |  | 0 | 0 | 0 | 1 |  | 0.67078 | 0.11158 |  |  | 0.11158 |  | 3 | 0
Lighting Load | [18 empty] | 0.87816 | 0.8 |  |  |  |  | 250 | 1 | 85 |  |  | 3.0683 |  |  |  |  | 0 |  | 0.87816 | 0.87816 | 0.0981 | 0.14899 | 0.14899 |  | 0 |  | 206.9533 | 210 | 0
Wall socket |  |  | 75 | [15 empty] | 0.65862 | [5 empty] | 13.775 |  | 12.1607 |  |  | 0.87816 | 0.65862 |  |  |  | 0 |  | 0.65862 | 0.65862 | 0.0826 | 0.11158 | 0.11158 |  | 1 |  |  | 50 | 0
| 84P4 | No.8 Substation TR No8-4 Switchboard(New) ～#4P-1 | [9 empty] | AC power | 28.64 | 0.8 | 0.8 | 44.75 | 0.6 | 73.8184 | 2.7083 | [5 empty] | 600V CE(NE)-T |  |  |  | 206.9533 | 205.1708 | 75.7571 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 2.1915 | 0.17887 |  |  | 0.17887 | 206.9533 | 3 | 0
[13 empty] | 1.68 | 1 | 0.8 | 2.1 | 0.6 | 3.4641 | [11 empty] | 97.7004 | 926.3919 |  |  |  | 0 | 0 | 0 | 1 |  | 1.6309 | 0.13384 |  |  | 0.13384 |  | 3 | 0
[12 empty] | Exhaust fan | 1.2 | 0.8 | 0.8 | 1.875 | 0.05 | 0.25775 | 2.1666 | 0.8 |  |  |  |  | 60 | 1 | 38 |  |  | 2.2996 |  |  |  |  | 0 |  | 2.1666 | 2.1666 | 0.397 | 0.17887 | 0.17887 |  | 0 |  | 206.9533 | 210 | 0
|  |  | 75 | [15 empty] | 1.625 | [5 empty] | 24.9217 |  | 5.9565 |  |  | 2.1666 | 1.625 |  |  |  | 0 |  | 1.625 | 1.625 | 0.0905 | 0.13384 | 0.13384 |  | 1 |  |  | 50 | 0
| 84P5 | No.8 Substation TR No8-4 Switchboard(New) ～R-1 | [9 empty] | Chiller | 64 | 0.8 | 0.8 | 100 | 0.6 | 164.9572 | 1.2667 | [5 empty] | 600V CE(NE)-T |  |  |  | 206.9533 | 204.5525 | 161.4815 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 1.0265 | 0.19476 |  |  | 0.19476 | 206.9533 | 3 | 0
[12 empty] | (Air cooling) | 0.4 | 1 | 0.8 | 0.5 | 0.6 | 0.82479 | [11 empty] | 97.4059 | 850.6351 |  |  |  | 0 | 0 | 0 | 1 |  | 0.7673 | 0.1458 |  |  | 0.1458 |  | 3 | 0
[19 empty] | 1.0134 | 0.8 |  |  |  |  | 150 | 1 | 50 |  |  | 2.5941 |  |  |  |  | 0 |  | 1.0134 | 1.0134 | 0.159 | 0.19476 | 0.19476 |  | 0 |  | 206.9533 | 210 | 0
|  |  | 75 | [15 empty] | 0.76003 | [5 empty] | 13.1332 |  | 7.266 |  |  | 1.0134 | 0.76003 |  |  |  | 0 |  | 0.76003 | 0.76003 | 0.0839 | 0.1458 | 0.1458 |  | 1 |  |  | 50 | 0
| 84P6 | No.8 Substation TR No8-4 Switchboard(New) ～R-5 | [9 empty] | Chiller | 64 | 0.8 | 0.8 | 100 | 0.6 | 164.9572 | 1.2667 | [5 empty] | 600V CE(NE)-T |  |  |  | 206.9533 | 204.3154 | 161.2944 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 1.0278 | 0.24037 |  |  | 0.24037 | 206.9533 | 3 | 0
[12 empty] | (Air cooling) | 0.4 | 1 | 0.8 | 0.5 | 0.6 | 0.82479 | [11 empty] | 97.2931 | 689.1536 |  |  |  | 0 | 0 | 0 | 1 |  | 0.76803 | 0.18001 |  |  | 0.18001 |  | 3 | 0
[19 empty] | 1.0134 | 0.8 |  |  |  |  | 150 | 1 | 55 |  |  | 2.7069 |  |  |  |  | 0 |  | 1.0134 | 1.0134 | 0.159 | 0.24037 | 0.24037 |  | 0 |  | 206.9533 | 210 | 0
|  |  | 75 | [15 empty] | 0.76003 | [5 empty] | 14.4465 |  | 7.9925 |  |  | 1.0134 | 0.76003 |  |  |  | 0 |  | 0.76003 | 0.76003 | 0.0839 | 0.18001 | 0.18001 |  | 1 |  |  | 50 | 0
Drop down LIST | 84P7 | No.8 Substation TR No8-4 Switchboard(New) ～#4P-2 | [9 empty] | AC power | 81.8 | 0.8 | 0.8 | 127.8125 | 0.6 | 210.8359 | 0.99215 | [5 empty] | 600V CE(NE)-T |  |  |  | 206.9533 | 204.4015 | 206.018 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 0.80372 | 0.31374 |  |  | 0.31374 | 206.9533 | 3 | #REF!
construction of cable | [12 empty] | 0.4 | 1 | 0.8 | 0.5 | 0.6 | 0.82479 | [11 empty] | 97.3341 | 527.8594 |  |  |  | 0 | 0 | 0 | 1 |  | 0.60261 | 0.23511 |  |  | 0.23511 |  | 3 | 0
[19 empty] | 0.79372 | 0.8 |  |  |  |  | 200 | 1 | 50 |  |  | 2.6659 |  |  |  |  | 0 |  | 0.79372 | 0.79372 | 0.121 | 0.31374 | 0.31374 |  | 0 |  | 206.9533 | 210 | 0
Cabletray |  |  | 75 | [15 empty] | 0.59529 | [5 empty] | 9.9945 |  | 7.3179 |  |  | 0.79372 | 0.59529 |  |  |  | 0 |  | 0.59529 | 0.59529 | 0.0845 | 0.23511 | 0.23511 |  | 1 |  |  | 50 | 0
Subter- ranean | 84P8 | No.8 Substation TR No8-4 Switchboard(New) ～#5P-2 | [9 empty] | AC power | 28.51 | 0.8 | 0.8 | 44.5469 | 0.6 | 73.4833 | 2.5437 | [5 empty] | 600V CE(NE)-T |  |  |  | 206.9533 | 203.7766 | 80.1094 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 2.077 | 0.51464 |  |  | 0.51464 | 206.9533 | 3 | 0
Under drain | [12 empty] | 4.4 | 1 | 0.8 | 5.5 | 0.6 | 9.0726 | [11 empty] | 97.0365 | 321.8414 |  |  |  | 0 | 0 | 0 | 1 |  | 1.5363 | 0.38553 |  |  | 0.38553 |  | 3 | 0
Openpit | [18 empty] | 2.035 | 0.8 |  |  |  |  | 60 | 1 | 64 |  |  | 2.9635 |  |  |  |  | 0 |  | 2.035 | 2.035 | 0.397 | 0.51464 | 0.51464 |  | 0 |  | 206.9533 | 210 | 0
Exposure piping |  |  | 75 | [15 empty] | 1.5262 | [5 empty] | 41.9734 |  | 10.032 |  |  | 2.035 | 1.5262 |  |  |  | 0 |  | 1.5262 | 1.5262 | 0.0905 | 0.38553 | 0.38553 |  | 1 |  |  | 50 | 0
Conceal. piping | 84P9 | No.8 Substation TR No8-4 Switchboard(New) ～Control board (Existing) | [9 empty] | AC power | 96.95 | 0.8 | 0.8 | 151.4844 | 0.6 | 249.8844 | 0.84039 | [5 empty] | 600V CE(NE)-T |  |  |  | 206.9533 | 203.1505 | 241.734 |  |  |  | 0 | 0 | 0 | 1.7321 |  | 0.68414 | 0.68414 |  |  | 0.68414 | 206.9533 | 3 | 0
[30 empty] | 96.7383 |  |  |  |  | 0 | 0 | 0 | 1 |  | 0.51468 | 0.51468 |  |  | 0.51468 |  | 3 | 0
[19 empty] | 0.67231 | 0.8 |  |  |  |  | 250 | 1 | 73 |  |  | 3.2617 |  |  |  |  | 0 |  | 0.67231 | 0.67231 | 0.0981 | 0.68414 | 0.68414 |  | 0 |  | 206.9533 | 210 | 0
|  |  | 75 | [15 empty] | 0.50423 | [5 empty] | 11.8303 |  | 10.4439 |  |  | 0.67231 | 0.50423 |  |  |  | 0 |  | 0.50423 | 0.50423 | 0.0826 | 0.51468 | 0.51468 |  | 1 |  |  | 50 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 2 |  |  | 0 | 0
|  | No.8 Substation TR No.8-5 SC: 75KVar | [33 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 3 |  |  | 0 | 0
| 85P1 | No.8 Substation TR No8-5 Switchboard(New) ～CHDY Analysis meter | 3 | φ | 3 | W | 210 | V | oil cooled type | 1 | 75 | Test machine | 216 | 1 | 0.8 | 270 | 0.7 | 519.6152 | 0.40415 | [5 empty] | 600V CE(NE)-T |  |  |  | 207.4202 | 201.9729 | 499.7534 | MCCB-3P |  | Load factor of transformer | 0 | 0 | 0.98189 | 1.7321 |  | 0.33211 | 0.30361 |  |  | 0.43864 | 207.4202 | 3 | 0
[10 empty] | 3.1941 | [18 empty] | 546.8072 | 96.1776 | 546.8072 |  |  | 55.15 ％ | 0 | 0 | 0 | 1 |  | 0.24893 | 0.2274 |  |  | 0.12442 |  | 3 | 0
|  |  | 50 | [5 empty] | 300 | [9 empty] | 0.32332 | 0.8 |  |  |  |  | 200 | 2 | 88 |  | 454.9218 | 3.8224 |  | 800 | 800 |  | 1.5 | 0.0038192 | 0.32332 | 0.32332 | 0.121 | 0.30361 | 0.30361 |  | 0 | 0.44246 | 207.4202 | 210 | 0
|  |  | 75 | [5 empty] | 824.7861 | [9 empty] | 0.24249 | [5 empty] | 8.7951 |  | 6.4398 |  |  | 0.32332 | 0.24249 |  |  |  | 2.82 | 0.00718 | 0.24249 | 0.24249 | 0.0845 | 0.2274 | 0.2274 |  | 3 | 0.1316 |  | 50 | 0
| 85P2 | No.8 Substation TR No8-5 Switchboard(New) ～CVT equipment | [9 empty] | Test machine | 20 | 1 | 0.8 | 25 | 0.7 | 48.1125 | 4.3648 | [5 empty] | 600V CE(NE)-T |  |  |  | 207.4202 | 205.3804 | 47.0541 | MCCB-3P |  |  | 0 | 0 | 0 | 1.7321 |  | 3.5377 | 3.5377 |  |  | 3.5377 | 207.4202 | 3 | 0
[30 empty] | 97.8002 |  |  |  |  | 0 | 0 | 0 | 1 |  | 2.6298 | 2.6298 |  |  | 2.6298 |  | 3 | 0
[19 empty] | 3.4918 | 0.8 |  |  |  |  | 60 | 1 | 70 |  |  | 2.1998 |  | 100 | 75 |  | 0 |  | 3.4918 | 3.4918 | 0.397 | 3.5377 | 3.5377 |  | 0 |  | 207.4202 | 210 | 0
|  |  | 75 | [15 empty] | 2.6189 | [5 empty] | 45.9084 |  | 10.9725 |  |  | 3.4918 | 2.6189 |  |  |  | 0 |  | 2.6189 | 2.6189 | 0.0905 | 2.6298 | 2.6298 |  | 3 |  |  | 50 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 4 |  |  | 0 | 0
[36 empty] | 0 | 0 | 0 | [7 empty] | 0 | 0
[36 empty] | 0 | 0 | 1.7321 | [7 empty] | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 1 |  |  | 0 | 0
[38 empty] | 1e+30 |  |  |  |  | 5 |  |  | 0 | 0
[38 empty] | 1e+30 | [7 empty] | 0 | 0
|  | TGCRDL Relocation Project | [13 empty] | ESE-VD4 Exchange circuit analysis calculation | [5 empty] | Co.,Ltd. Yoshimura Airchitecture Design Office | [6 empty] | K,Yoshimura |  | K,Sakai |  |  | Terminal voltage -10 (Standard)
Note on B12: Drop down LIST An addition, change, and deletion can do this registration cell.
Note on B46: Drop down LIST An addition, change, and deletion can do this registration cell.
Note on C8: Printing range
Note on F13: Please input the temperature of conductor for calculation. (Each line) -100[℃] ～ +300[℃] Attention: It calculates by 0[℃] if it does not input. Ａｂｏｕｔ ｔｈｅ ｔｅｍｐｅｒａｔｕｒｅ ｏｆ ｃｏｎｄｕｃｔｏｒ The degree 20[℃] is standard temperature. Generally, this temperature is 50-60 [℃] except for a cold district. Please decide on reference by carrying out the maximum per- mission temperature of a conductor.
Note on L3: It can use for the power transmission voltage at the time of regular of an independent trunk and a branch trunk, received voltage, load current, the check of power factor, the determination of series capacitor capacity, etc. Comment ■ is the object for cells which needs an input． ■ is an explanatory note etc. Input cell ■ should input a required matter. Calculation cell ■ is an automatic calculation cell, an input is impossible.
Note on L11: ↓Please choose out of a drop down list. When Liszt does not have [except oil cooled type and (F)-molded type], please perform after inputting data into the "transformer USER" of DATA Table.
Note on L13: Following transformer data is registered into DATA Table. （50/60Hz） ３φ３Ｗ－２０ ～ １０００［ＫＶＡ］ １φ３Ｗ－１０ ～ ５００［ＫＶＡ］ An exact value will be calculated if the change correction of the %R and %X of an adoption transformer is made by DATA Table. Calculation of transformer rated current is depended below. In the case of ３φ：TRcap／(√3 x Es) In the case of １φ：TRcap／ Es TRcap：Capacity of TR. Es：Secondary voltage of TR.
Note on M11: When a transformer is parallel operation, please input the number of a parallel transformer.
Note on N6: High-voltage Capacitor［Nichicon Corp.1991.5］ 3300V，6600V-50Hz，60Hz（no Series reactor） 50, 75,100,150,200,250,300 [KVar] 3300V，6600V-50Hz，60Hz（Series reactor 6％） 50, 75,100,150,200,250,300,400,500,600, 700,750,800,900,1000[KVar] 3300V，6600V-50Hz，60Hz（Series reactor 13％） 50, 75,100,150,200,250,300,400,500[KVar]
Note on N7: Low-voltage Capacitor［Nichicon Corp.1991.5］ 200V，220V-50Hz，60Hz（no Series reactor） 10, 15, 20, 25, 30, 50[KVar] 200V，220V-50Hz，60Hz（Series reactor ６％） 10, 15, 20, 25, 30, 40, 50, 75,100[KVar] 400，415，440，460V-50Hz，60Hz（no Series reactor） 10, 15, 20, 25, 30, 50, 75,100,150[KVar] 400，415，440，460V-50Hz，60Hz（Series reactor 6％） 10, 15, 20, 25, 30, 50, 75,100,150,200 250,300[KVar]
Note on N10: Ｓｅｒｉｅｓ ｐｏｗｅｒ ｃａｐａｃｉｔｏｒ When average power factor of total load is bad (delay), SC improves power factor, and it installs the electric power transfor- mer by the side of power distribution in order to operate efficiently.
Note on O10: When you perform accumulation calculation, be careful of the following point. Trunk branch etc., when you accumulate the voltage drop value of each section, please use four lines each of a "cell" continuously. When you move to independent trunk calculation or next another calculation, four or more lines should vacate and please be sure to input a cell.
Note on O11: Please choose out of a drop down list.
Note on Q11: In the case of induction motor load, please input in the range of ０＜～１．０００ In the case of other loads, please input ”１”
Note on R11: Please input the value of the range of ０＜～１．０００
Note on S11: Iｎｐｕｔ ＫＶＡ Input ＫＶＡ＝Output ＫＷ／（ｃｏｓφｘη） cosφ ：Power factor of Load η ：Efficiency of Load
Note on W10: Load side Series Power Capacitor SC improves delay power factor of induc- tive load, reduces voltage drop of a trunk, and it installs it in order to prevent the fall of primary voltage.
Note on X11: Please choose out of a drop down list. In inputting the size which is not in a data table, please register R and X (50Hz) of the cable into a data table.
Note on Z11: Please input the fruit length meter of a cable.
Note on AA10: Please choose out of a drop down list.
Note on AB11: Please choose out of a drop down list. In inputting the size which is not in a data table, please register R and X (50Hz) of the cable into a data table.
Note on AD11: Please input the fruit length meter of a cable.
Note on AE10: Please choose out of a drop down list.
Note on AF10: Secondary transformer side voltage ［Ｖ］
Note on AF13: Voltage of the circuit diagram EB section ［Ｖ］
Note on AG11: Percent to power supply voltage [％]
Note on AG12: Percent of line voltage drop to power supply voltage [％]
Note on AJ11: ↓Please choose out of a drop down list. The important matter about selection of the frame / trip value of MCCB １） The check of interception capacity ２） The characteristic and the temperature conditions of MCCB ３） Grasp of the real load current which took into consideration the demand factor, load factor, divercity factor,voltage regulation rate of transformer, unbalance factor, etc. at the time of regular operation of a motor, at the time of starting of a motor. Frame value [A] of MCCB（Ｍｏｌｄｅｄ ｃａｓｅ ｃｉｒｃｕｉｔ ｂｒｅａｋｅｒ） ３０， ５０， ６０， １００， ２２５， ２５０， ４００， ６００， ８００，１０００， １２００，１６００，２０００，２５００，３０００， ３２００，４０００ Frame value [A] of ＡＣＢ（Ａｉｒ ｃｉｒｃｕｉｔ ｂｒｅａｋｅｒ） ６３０，１０００，１２５０，１６００，２０００， ２５００，３２００，４０００，５０００，６３００
Note on AJ12: Please choose out of a drop down list.
Note on AJ13: Please choose out of a drop down list.
Input cell
Exchange circuit analisys calculation -VD４
２００２ Ａｕｇ． Ｖｅｒ ２．0 by ＥＳＥ SERVICE
Automatic display
A "comment" will be displayed if cursor is brought close to the cell of upper right red.
Approved
Checked

## DATA Table
Attention ⇒
TR | 1φ oil cooled-50Hz |  |  | TR | 1φ molded-50Hz |  |  | TR | 1φ oil cooled-60Hz |  |  | TR | 1φ molded-60Hz |  |  | IV (Piping) |  |  | 600V CV-T
Capa. | ％ R | ％ X | ％ Z | Capa. | ％ R | ％ X | ％ Z | Capa. | ％ R | ％ X | ％ Z | Capa. | ％ R | ％ X | ％ Z | Cross | Resistance | Reactance | Cross | Resistance | Reactance
10 | 2.01 | 1.74 | 2.6585 | 10 | 2.72 | 3.5 | 4.4327 | 10 | 1.92 | 1.93 | 2.7224 | 10 | 2.72 | 3.5 | 4.4327 | section | [60℃] | [50Hz] | section | [90℃] | [50Hz]
20 | 1.77 | 1.82 | 2.5388 | 20 | 1.99 | 4.64 | 5.0487 | 20 | 1.68 | 2.04 | 2.6427 | 20 | 1.99 | 4.64 | 5.0487 |  | [Ω/Km] | [Ω/Km] |  | [Ω/Km] | [Ω/Km]
30 | 1.56 | 2.37 | 2.8373 | 30 | 1.56 | 4.28 | 4.5554 | 30 | 1.51 | 2.6 | 3.0067 | 30 | 1.56 | 4.28 | 4.5554 | 2 | 10.7 | 0.0992 | 8 | 3.01 | 0.114
50 | 1.43 | 2.27 | 2.6829 | 50 | 1.81 | 3.54 | 3.9759 | 50 | 1.39 | 2.55 | 2.9042 | 50 | 1.81 | 3.54 | 3.9759 | 3.5 | 6.02 | 0.0914 | 14 | 1.71 | 0.107
75 | 1.53 | 1.95 | 2.4786 | 75 | 1.54 | 3.6 | 3.9156 | 75 | 1.43 | 2.15 | 2.5821 | 75 | 1.54 | 3.6 | 3.9156 | 5.5 | 3.85 | 0.0914 | 22 | 1.08 | 0.102
100 | 1.54 | 2.29 | 2.7597 | 100 | 1.57 | 3.88 | 4.1856 | 100 | 1.42 | 2.54 | 2.91 | 100 | 1.57 | 3.88 | 4.1856 | 8 | 2.67 | 0.0914 | 38 | 0.626 | 0.0939
150 | 1.41 | 2.36 | 2.7491 | 150 | 1.41 | 4.33 | 4.5538 | 150 | 1.37 | 2.73 | 3.0545 | 150 | 1.41 | 4.33 | 4.5538 | 14 | 1.5 | 0.083 | 60 | 0.397 | 0.0905
200 | 1.35 | 2.7 | 3.0187 | 200 | 1.35 | 4.88 | 5.0633 | 200 | 1.31 | 3.14 | 3.4023 | 200 | 1.35 | 4.88 | 5.0633 | 22 | 0.953 | 0.0858 | 100 | 0.24 | 0.0883
300 | 1.31 | 3.7 | 3.9251 | 300 | 1.11 | 4.99 | 5.112 | 300 | 1.29 | 4.28 | 4.4702 | 300 | 1.11 | 4.99 | 5.112 | 38 | 0.563 | 0.0761 | 150 | 0.159 | 0.0839
500 | 1.11 | 4.11 | 4.2573 |  |  |  |  | 500 | 1.1 | 4.75 | 4.8757 |  |  |  |  | 60 | 0.351 | 0.0786 | 200 | 0.121 | 0.0845
[16 empty] | 100 | 0.209 | 0.0761 | 250 | 0.0981 | 0.0826
[16 empty] | 150 | 0.137 | 0.0744 | 325 | 0.0765 | 0.0807
[16 empty] | 200 | 0.107 | 0.074 | 400 | 0.0634 | 0.0792
[16 empty] | 250 | 0.084 | 0.0724 | 500 | 0.052 | 0.0795
TR | 3φ oil cooled-50Hz |  |  | TR | 3φ molded-50Hz |  |  | TR | 3φ oil cooled-60Hz |  |  | TR | 3φ molded-60Hz |  |  | 325 | 0.0666 | 0.0719 | 600 | 0.0448 | 0.0785
Capa. | ％ R | ％ X | ％ Z | Capa. | ％ R | ％ X | ％ Z | Capa. | ％ R | ％ X | ％ Z | Capa. | ％ R | ％ X | ％ Z
20 | 2.14 | 0.98 | 2.3537 | 20 | 3.39 | 2.82 | 4.4096 | 20 | 1.97 | 1.01 | 2.2138 | 20 | 3.16 | 3.03 | 4.378
30 | 1.91 | 1.09 | 2.1991 | 30 | 2.83 | 2.49 | 3.7695 | 30 | 1.78 | 1.24 | 2.1693 | 30 | 2.84 | 3.11 | 4.2116
50 | 1.81 | 1.31 | 2.2343 | 50 | 1.98 | 3.1 | 3.6784 | 50 | 1.7 | 1.46 | 2.2409 | 50 | 1.93 | 3.12 | 3.6687 | 600V CV-2C/3C |  |  | USER |  | ⇒
75 | 1.78 | 1.73 | 2.4822 | 75 | 1.7 | 3.6 | 3.9812 | 75 | 1.64 | 1.93 | 2.5327 | 75 | 1.66 | 4.17 | 4.4883 | Cross | Resistance | Reactance | Cross | Resistance | Reactance
100 | 1.73 | 1.74 | 2.4537 | 100 | 1.87 | 3.83 | 4.2621 | 100 | 1.6 | 1.93 | 2.507 | 100 | 1.91 | 4.4 | 4.7967 | section | [90℃] | [50Hz] | section | [90℃] | [50Hz]
150 | 1.61 | 1.91 | 2.498 | 150 | 1.57 | 3.93 | 4.232 | 150 | 1.5 | 2.12 | 2.597 | 150 | 1.56 | 4.69 | 4.9426 |  | [Ω/Km] | [Ω/Km] |  | [Ω/Km] | [Ω/Km]
200 | 1.63 | 2.6 | 3.0687 | 200 | 1.49 | 4.35 | 4.5981 | 200 | 1.53 | 2.9 | 3.2789 | 200 | 1.44 | 4.88 | 5.088 | 2 | 12 | 0.0992 | 2
300 | 1.5 | 2.82 | 3.1941 | 300 | 1.44 | 4.43 | 4.6582 | 300 | 1.41 | 3.26 | 3.5519 | 300 | 1.34 | 5.07 | 5.2441 | 3.5 | 6.76 | 0.0914 | 3.5
500 | 1.25 | 4.06 | 4.2481 | 500 | 1.07 | 4.09 | 4.2276 | 500 | 1.18 | 4.61 | 4.7586 | 500 | 1.06 | 5.47 | 5.5718 | 5.5 | 4.34 | 0.0914 | 5.5
750 | 1.31 | 4.92 | 5.0914 |  |  |  |  | 750 | 1.24 | 5.35 | 5.4918 |  |  |  |  | 8 | 3.01 | 0.087 | 8 | 3.01 | 0.114
1000 | 1.19 | 5.02 | 5.1591 |  |  |  |  | 1000 | 1.12 | 5.68 | 5.7894 |  |  |  |  | 14 | 1.71 | 0.0828 | 14 | 1.71 | 0.107
[16 empty] | 22 | 1.08 | 0.082 | 22 | 1.08 | 0.102
15000 | [7 empty] | 15000 |  | 12 | 12 |  |  |  |  | 38 | 0.626 | 0.0771 | 38 | 0.626 | 0.0939
[16 empty] | 60 | 0.397 | 0.0773 | 60 | 0.397 | 0.0905
[16 empty] | 100 | 0.24 | 0.0777 | 100 | 0.24 | 0.0883
TR | 3φ User-50Hz |  | ⇒ | [12 empty] | 150 | 0.159 | 0.0747 | 150 | 0.159 | 0.0839
Capa. | ％ R | ％ X | ％ Z | [12 empty] | 200 | 0.121 | 0.0757 | 200 | 0.121 | 0.0845
[16 empty] | 250 | 0.0985 | 0.0742 | 250 | 0.0981 | 0.0826
[16 empty] | 325 | 0.0771 | 0.0725 | 325 | 0.0765 | 0.0807
Data Sheet［ＶＤ４］
Note on B1: this -- Protection of DATA Table and a cell is not carried out. Management of DＡTA Be careful enough.
Note on E36: For USER registration
Note on AB23: For USER registration